## Slide 1
SHOP DRAWINGS — ELECTRICAL / AGL SCOPE
RECTIFICATION OF TWY E BETWEEN E4 & E6 (ADIA)
AGL WORKS AT THREE (3) MILLING LOCATIONS — FIELD CONDITION SCOPE
Document No.
[XXX-ELE-SHD-1001 / 1002 / 1003] · Revision P06 (EDITABLE ISSUE)
Basis of scope
Field verification sheets: Document_3 (LOC-01) · Second_milling_area rev _1 (LOC-02/03) · Duct geometry: ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf
Base layer
As-built AGL fitting positions (per assets_20260726120533.xlsx). AS PLOTTED they are ZIA LOCAL PROJECT GRID (m), matching the ADA source drawing to sub-millimetre — NOT UTM 40N. The Rev P05 EPSG:32640 label was incorrect — see sheet 6.
Prepared by
Mohammed — AGL Team Leader, ADB SAFEGATE AGL Team · Issued 28.07.2026
REV P06 — the "indicative duct" construction lines of Rev P05 (straight lines from each light to its nearest pit) are removed and replaced with the real as-built duct, ductbank, conduit and sawcut geometry from the ADA source drawing, registered onto each sheet to sub-millimetre. Every element remains a native editable PowerPoint shape. Provenance, registration residuals and limits: sheet 6.

## Slide 2
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 1 · DWG NO [XXX-ELE-SHD-1001] REV P06
ZIA LOCAL PROJECT GRID (m) — NOT UTM, NOT SURVEYED · FRAME = 102.1 m ACROSS · NOT TO SCALE WHEN EDITED
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
AGL WORKS AREA — FIELD CONDITION (425.3 m² TOTAL)
RRM.76
RRM.282
TCCECH.04.018
RRM.539
RRM.540
RRM.541
RRM.636
TCC103.12.019
TCC103.11.019
TCC103.11.020
TEC102.02.047
TEC102.02.048
TEC102.02.049
HH.E6.033
TCCECH.03.017
TCCECH.04.016
TCCECH.03.016
TCCECH.04.015
TCCECH.03.015
SBC102.02.027
TCC103.11.027
TCCECH.03.038
TCCECH.04.037
TCCECH.03.039
TCCECH.04.038
TCCECH.04.019
TCCECH.03.020
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
HH.E6.038
HH.E6.037
HH.E6.036
HH.E6.035
HH.E6.040
HH.E6.041
HH.E6.042
HH.E6.034
HH.E6.032
HH.E6.039
P6.009
P6.038
MH.E.024
MH.E.014
X_CV_STH_PITS &.23918
SGC102.02.017
SGC102.02.016
TEC102.02.050
SBC102-02/024
SBC102-01/027
SBC102-02/025
SBC102-01/028
SBC102-02/026
SBC102-01/029
TCCECH-04/034
TCCECH-03/036
TCCECH-04/035
TCCECH-03/037
TCCECH-04/036
SBC102-02/027
TCCECH-03/035
TCCECH-03/018
SBC102-01/026
LOCATION 1 — 1001 · REV P06 (EDITABLE)
SCOPE PER FIELD SHEET Document_3 — FIELD CONDITION GOVERNS
Frame 102.1 m across · ZIA local grid (m) · duct geometry from Z1-Z2-Z3-MTA_SEGMENTATION source dwg · Rev P06 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
CORE OUT SHALLOW BASE + NEW CABLE: 11 No.
• VIA DUCT (6): SBC102-02/024, 01/027, 02/025, 01/028, 02/026, 01/029
• VIA SAWCUT (5): TCCECH-04/034, 03/036, 04/035, 03/037, 04/036
NEW SECONDARY CABLE ONLY: 3 No.
• SBC102-02/027 (DUCT) · TCCECH-03/035, 03/018 (SAWCUT — bases OK, verify at cut line)
FIELD VERIFIED NOT AFFECTED: SBC102-01/026 (no works)
TCC103 FITTINGS NOT IN FIELD SCOPE — SHOWN AS EXISTING ONLY
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
SITE RECORD 23.07.2026: 9 cored + 2 reinstatement already worked
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition. Coring at Location 1 only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
CORE OUT + NEW CABLE (DUCT)
CORE OUT + NEW CABLE (SAWCUT)
NEW SEC. CABLE ONLY (DUCT)
NEW SEC. CABLE ONLY (SAWCUT)
FIELD VERIFIED — NOT AFFECTED
AS-BUILT DUCT / DUCTBANK 4×110 · 6×110
AS-BUILT SECONDARY CONDUIT
AGL WORKS AREA (GOVERNING)
TAXIWAY CENTRELINE (AS-BUILT)
STOP BAR (AS-BUILT)
TWY EDGE / PAVEMENT (INDICATIVE 23 m)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
TWY CENTRELINE LIGHT (31)
TWY EDGE LIGHT (4)
STOP BAR LIGHT (8)
RUNWAY GUARD LIGHT / RRM (6)
SIGN FOUNDATION (2)
HANDHOLE (HH) (11)
TRANSFORMER HH (SEC. FEED HUB) (5)
MANHOLE (MH) (2)
TRANSFORMER MH (SEC. FEED) (2)
EARTHING POINT (10)
EARTHING PIT (1)

## Slide 3
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 2 · DWG NO [XXX-ELE-SHD-1002] REV P06
ZIA LOCAL PROJECT GRID (m) — NOT UTM, NOT SURVEYED · FRAME = 108.9 m ACROSS · NOT TO SCALE WHEN EDITED
P2.002
AGL WORKS AREA — FIELD CONDITION (257.1 m² TOTAL)
RRM.545
RRM.546
RRM.554
RRM.556
X_CV_STH_PITS &.24043
TCCECH.03.010
TCCECH.04.009
TCCECH.04.007
TCCECH.03.007
TCCECH.04.006
TCCECH.03.006
TCCECH.03.008
TCCECH.04.008
TCCECH.03.009
P2.002
HH.E.055
HH.E.056
TCCECH-03/007
TCCECH-04/007
TCCECH-03/008
TCCECH-04/008
TCCECH-03/009
RRM.555
LOCATION 2 — 1002 · REV P06 (EDITABLE)
SCOPE PER FIELD SHEET Second_milling_area rev _1 — FIELD CONDITION GOVERNS
Frame 108.9 m across · ZIA local grid (m) · duct geometry from Z1-Z2-Z3-MTA_SEGMENTATION source dwg · Rev P06 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
NEW SECONDARY CABLE ONLY (VIA DUCT): 5 No.
• TCCECH-03/007, 04/007, 03/008, 04/008, 03/009
NO SHALLOW BASES AFFECTED AT THIS LOCATION
SECONDARY DUCT (AS-BUILT): 5 SEPARATE HOME RUNS FROM ONE TRANSFORMER HANDHOLE — NOT A CHAINED RUN. 20.5 / 21.1 / 29.1 / 30.3 / 41.5 m = 142.5 m TOTAL. RE-PRICE — SEE SHEET 7.
(Rev P06 chained-run assumption superseded by the source drawing — see sheet 7)
RRM.555 (0.41 m from cut): REMOVE / PROTECT BEFORE SAWCUT, RE-FIX AFTER PAVING
ISOLATE CIRCUITS: TCCECH.03, TCCECH.04
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition. Coring at Location 1 only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
NEW SEC. CABLE ONLY (DUCT)
RRM — REMOVE / PROTECT / RE-FIX
AS-BUILT DUCT / DUCTBANK 4×110 · 6×110
AS-BUILT SECONDARY CONDUIT
AGL WORKS AREA (GOVERNING)
TAXIWAY CENTRELINE (AS-BUILT)
TWY EDGE / PAVEMENT (INDICATIVE 23 m)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
TWY CENTRELINE LIGHT (9)
RUNWAY GUARD LIGHT / RRM (5)
HANDHOLE (HH) (2)
TRANSFORMER HH (SEC. FEED HUB) (1)
EARTHING POINT (3)
EARTHING PIT (1)

## Slide 4
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 3 · DWG NO [XXX-ELE-SHD-1003] REV P06
ZIA LOCAL PROJECT GRID (m) — NOT UTM, NOT SURVEYED · FRAME = 95.1 m ACROSS · NOT TO SCALE WHEN EDITED
P4.037
HH.E.058
AGL WORKS AREA — FIELD CONDITION (676.7 m² TOTAL)
RRM.283
P4.036.399
TCCECH.04.005
TCCECH.04.004
RRM.547
RRM.548
RRM.558
RRM.559
RRM.655
RRM.669
HH.E.144
TCCECH.03.006
TCCECH.03.004
TCCECH.04.003
TCCECH.03.003
TCCECH.04.002
TCCECH.03.005
TCCECH.05.034
TCCECH.05.033
TCCECH.06.035
TCCECH.06.036
EL.EBASE.13328
EL.EBASE.13329
EL.EBASE.13330
EL.EBASE.13331
TCCECH.03.002
SBC102.01.040
SBC102.02.037
SBC102.01.041
SBC102.02.038
TCC102.01.052
TCC102.02.050
TCCECH.03.001
TCCECH.05.016
TCCECH.05.017
TCCECH.06.019
TCCECH.06.017
TCCECH.06.018
TCCECH.04.001
TCCECH.05.018
P4.037
P4.039
HH.E.057
HH.E.061
HH.E.060
HH.E4.010
HH.E.058
HH.E.059
P4.041
MH.E.015
MH.E.023
SGC102.02.015
SGC102.02.014
SBC102-01/038
SBC102-01/039
SBC102-02/035
SBC102-02/036
SBC102-01/040
SBC102-01/041
SBC102-02/037
SBC102-02/038
TCCECH-03/002
TCCECH-04/002
TCCECH-03/003
TCCECH-04/003
RRM.557
RRM.670
LOCATION 3 — 1003 · REV P06 (EDITABLE)
SCOPE PER FIELD SHEET Second_milling_area rev _1 — FIELD CONDITION GOVERNS (rev _1 supersedes earlier all-NO rev)
Frame 95.1 m across · ZIA local grid (m) · duct geometry from Z1-Z2-Z3-MTA_SEGMENTATION source dwg · Rev P06 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
NO CORING AT THIS LOCATION — SECONDARY CABLES ONLY (12 RUNS)
NEW CABLE VIA SAWCUT: 4 No. — SBC102-01/038, 01/039, 02/035, 02/036
(EP7 STOP BAR — bases per field rev _1: remove fitting & protect base, NO coring)
NEW SECONDARY CABLE ONLY (VIA DUCT): 8 No.
• SBC102-01/040, 01/041, 02/037, 02/038, TCCECH-03/002, 04/002, 03/003, 04/003
RRM.557 (0.07 m — treat as within works) & RRM.670: REMOVE / PROTECT / RE-FIX
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition. Coring at Location 1 only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
NEW SEC. CABLE ONLY (SAWCUT)
NEW SEC. CABLE ONLY (DUCT)
RRM — REMOVE / PROTECT / RE-FIX
AS-BUILT DUCT / DUCTBANK 4×110 · 6×110
AS-BUILT SECONDARY CONDUIT
AGL WORKS AREA (GOVERNING)
TAXIWAY CENTRELINE (AS-BUILT)
STOP BAR (AS-BUILT)
TWY EDGE / PAVEMENT (INDICATIVE 23 m)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
TWY CENTRELINE LIGHT (23)
STOP BAR LIGHT (8)
RUNWAY GUARD LIGHT / RRM (9)
EXISTING LIGHT BASE (NO FITTING) (4)
SIGN FOUNDATION (2)
HANDHOLE (HH) (7)
TRANSFORMER HH (SEC. FEED HUB) (2)
MANHOLE (MH) (2)
TRANSFORMER MH (SEC. FEED) (2)
EARTHING POINT (7)

## Slide 5
CONSOLIDATED FIELD-GOVERNED SCOPE — TWY E (E4–E6) · REV P06
Loc | Asset | Works Action | Route | Remarks
LOC-01 | SBC102-02/024 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/027 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/025 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/028 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/026 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/029 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/034 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-03/036 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/035 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-03/037 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/036 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/027 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-01 | TCCECH-03/035 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-01 | TCCECH-03/018 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-01 | SBC102-01/026 | NOT AFFECTED | — | Field verified — no works
LOC-02 | TCCECH-03/007 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-04/007 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-03/008 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-04/008 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-03/009 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | RRM.555 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving
LOC-03 | SBC102-01/038 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-03 | SBC102-01/039 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/035 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/036 | NEW CABLE ONLY | Sawcut | Full manhole-to-light cable replacement
LOC-03 | SBC102-01/040 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-01/041 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/037 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/038 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-03/002 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-04/002 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-03/003 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-04/003 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | RRM.557 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving
LOC-03 | RRM.670 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving
Totals: 11 core-outs (Location 1 only) · 31 secondary cable runs · 3 RRMs · 1 field-verified not affected. · The "Route" column is carried over from Rev P05 and is NOT derived from the as-built duct data: per-asset attribution could not be established from the sheets (see sheet 6, limit d). Sheet-level duct schedule is on sheet 6.

## Slide 6
SHEET 6 — DUCT PROVENANCE & REGISTRATION VERIFICATION · TWY E (E4–E6) REV P06
1 · SOURCE OF THE DUCT GEOMETRY
Drawing: Z1-Z2-Z3-MTA_SEGMENTATION.dxf, issued by Abu Dhabi Airports. AC1032 (AutoCAD 2018), $INSUNITS = 6 (metres), 549 MB, 2,564 layers, 12 model-space xrefs all inserted at (0,0,0), scale 1, rotation 0.
Extracted population: 33,720 fixture INSERTs and 49,505 linear features (1,878 km), of which 17,101 features / 466 km are duct, ductbank, conduit, sawcut or secondary cable.
Duct type, bore and way-count are read from the layer name — that is the only place the drawing records them (e.g. CV_OUTER DUCT 4x110mm dia).
Extraction is reconciled against an independent per-layer entity census; every count above is asserted by an automated check, not read off by eye.
2 · HOW SHEETS 2–4 WERE TIED TO THE SOURCE DRAWING
The sheets carry no coordinate grid, so each was registered to the source drawing by matching the plotted AGL fitting pattern: type-matched 2-point RANSAC to find the correspondence, then a 4-parameter Helmert fit (translation, rotation, uniform scale) by least squares — not an affine, which would hide error as fake shear. Half the matched pairs were held back from the fit; the hold-out RMS below is the accuracy figure.
Sheet
Fitting symbols
in frame
Matched to source
within 50 mm
Fit RMS
HOLD-OUT RMS
(pairs never fitted)
Plotted scale
Frame on ground
LOC-01
64
37
0.4 mm
0.40 mm on 14
93,614 EMU/m
102.1 m
LOC-02
18
9
0.3 mm
0.46 mm on 4
87,716 EMU/m
108.9 m
LOC-03
59
11
58.2 mm
0.49 mm on 13
100,476 EMU/m
95.1 m
Rotation solved to +0.0001° / −0.000001° / +0.0027° and the y axis is mirrored — i.e. the sheets are plotted axis-aligned to the grid. Independent check: the deck's own "as-built taxiway centreline" polyline, never used in the fit, lands on source centreline fixtures at 0.3–0.4 mm median on LOC-01/02.
3 · FINDING — THE Rev P05 COORDINATE LABEL WAS WRONG
Rev P05 sheets state "UTM 40N (EPSG:32640) — AS-BUILT POSITIONS". They are not UTM. The plotted positions are ZIA local project grid metres (X ≈ 5,800–6,200, Y ≈ 54,400–54,700). UTM 40N here would read easting ~230,000–800,000 and northing ~2,650,000–2,750,000.
The source drawing carries no GEODATA object and no georeferencing of any kind, so no local→UTM transform can be derived from it. Rev P06 sheets are relabelled accordingly.
Consequence: any coordinate previously issued from Rev P05 as UTM — to ADA, Injaz or a contractor — needs withdrawing and re-checking against survey control.
4 · DUCT SCHEDULE — WHAT IS DRAWN ON EACH SHEET
LOC-01 — 59 segments, 1433 m inside the frame
Source layer (carries bore & way-count)
Draw
Segs
On sheet
CV-NEW SEC SAWCUT
23
606.7 m
CV-EX SEC CONDUIT
21
490.9 m
CV_INNER DUCT 4x110mm dia
3
84.6 m
CV_OUTER DUCT 4x110mm dia
2
81.5 m
CV_STH DUCT 6x110mm dia
1
65.6 m
CV_DUCT CROSSING 6x110mm dia
1
53.3 m
CV-NEW SEC CONDUIT
7
49.0 m
CV_GRND DUCT
1
1.5 m
LOC-02 — 13 segments, 349 m inside the frame
Source layer (carries bore & way-count)
Draw
Segs
On sheet
CV-EX SEC CONDUIT
10
230.7 m
CV_OUTER DUCT 4x110mm dia
1
110.8 m
CV-NEW SEC CONDUIT
1
6.2 m
CV_GRND DUCT
1
1.6 m
LOC-03 — 53 segments, 1104 m inside the frame
Source layer (carries bore & way-count)
Draw
Segs
On sheet
CV-EX SEC CONDUIT
29
541.5 m
CV-NEW SEC SAWCUT
11
259.1 m
CV_INNER DUCT 4x110mm dia
2
84.2 m
CV_OUTER DUCT 4x110mm dia
2
81.7 m
CV_DUCT CROSSING 6x110mm dia
1
57.8 m
CV-NEW SEC CONDUIT
5
46.6 m
CV_STH DUCT 6x110mm dia
1
30.4 m
CV_GRND DUCT
2
2.4 m
5 · LIMITS — READ BEFORE USING THIS GEOMETRY
a) Runs are fragments, not proven pulls. The duct lines are the individual LINE / LWPOLYLINE segments as drafted. No endpoint snapping or graph chaining has been done, so "handhole A to handhole B" is not established. Do not order cable to a length scaled off these sheets.
b) Coordinates are ZIA local grid, not surveyed and not UTM. Nothing here may be issued as a setting-out coordinate without an externally checked transform against ADA survey control.
c) Civil symbols are ~2.1–2.3 m off. Handhole, manhole, transformer-pit and RRM symbols on the sheets sit a mean 2.1–2.3 m (sd 0.3–0.45 m) from the source-drawing insertion point, while AGL light fittings match to sub-millimetre. Set out civil features from survey, not from these sheets.
d) Per-asset route attribution is NOT given. The consolidated table's "Route" column is unchanged from Rev P05. Attributing a specific duct layer to a named asset was attempted and rejected: the sheets' labels sit 3–8 m from their markers with neighbours only 10–15% further, and several markers resolve to the same label, so the assignment cannot be made from the drawing alone. It needs the source asset register, which is not in this data set.
e) Z values are unreliable in the source drawing. This is a 2D basemap only; take levels from survey.
f) Elements outside the twelve identity-inserted xrefs were excluded rather than drawn in the wrong place (3,375 geometry entities, 2,409 nested fixtures drawing-wide). If a duct looks absent in a given corner, check this first.
6 · THE GEOMETRY, IN THE SOURCE DRAWING'S OWN GRID
Reproduce: registration.json + sheet_ducts.json + duct_schedule.csv accompany this deck. Every figure on this sheet is computed from the source drawing, not transcribed.

## Slide 7
SHEET 7 — SECONDARY FEED TOPOLOGY (DERIVED) · STAR FROM TRANSFORMER HANDHOLES, NOT A CHAINED RUN
FINDING — THE Rev P05 LOC-02 SCOPE NOTE DESCRIBES THE WRONG TOPOLOGY
Rev P05, sheet 3 (LOC-02) states: "SECONDARY DUCT: CHAINED RUN HH.E.056 → 03/007 → 04/007 → 03/008 → 04/008 → 03/009 → HH.E.054". The source drawing shows no such chain.
Every affected light at LOC-02 is fed by its own individual conduit spur radiating from ONE transformer handhole — five separate home runs of 20.5, 21.1, 29.1, 30.3 and 41.5 m, 142.5 m in total, not a series loop between lights. This changes the cable quantity, the number of pulls and the isolation sequence. Re-price and re-plan LOC-02 before ordering cable.
WHY THIS ALSO PROVES THE GEOMETRY IS REAL
The conduit fragments were chained by snapping endpoints within 0.30 m. What comes out is not an arbitrary set of lines — it is a working secondary distribution network:
· Every hub node lands on a CV_ETRANS HH (existing transformer handhole) fixture at 0.000–0.002 m. Four hubs at LOC-01, one at LOC-02, two at LOC-03.
· 40 of 45 spurs terminating at a light land within 50 mm of that light's insertion point; most are exactly 0.00 m.
· Spur lengths are 6–42 m, consistent with transformer-handhole-to-light home runs.
Straight light-to-nearest-pit construction lines cannot produce that. Invented or inferred geometry would not terminate on fixture insertion points to the millimetre, nor converge specifically on transformer handholes rather than on any nearby pit.
METHOD AND ITS LIMIT
The source drawing stores these conduits as loose LINE / LWPOLYLINE segments with no connectivity. The chaining here is DERIVED, not read from the drawing: endpoints within 0.30 m were treated as one node, then each branch was walked outward from its hub until it reached a leaf or a junction.
Consequence: a spur length is the drawn geometry of a branch, not a proven pull. Two conduits passing within 0.30 m without physically joining would be merged; a genuine joint drawn with a wider gap would be split. Prove each run on site before ordering.
The 0.30 m tolerance sits far below the shortest real spur (6.2 m) and well above the drafting gaps observed. No spur changed hop count when the tolerance was varied between 0.10 and 0.50 m.
LOC-01 — DERIVED SPUR SCHEDULE
4 transformer-handhole hub(s) · 26 spurs · 516.9 m to lights
Length
Terminates at
Source layer
Offset
35.44 m
Taxiway centreline light
EL-TAXICL
5.13 m !
31.36 m
Taxiway centreline light
EL-TAXICL
0.00 m
30.40 m
Taxiway centreline light
EL-TAXICL
0.00 m
30.08 m
Taxiway centreline light
EL-TAXICL
0.06 m !
30.08 m
Stop bar light
EL-STOPBAR
0.04 m
27.17 m
Stop bar light
EL-STOPBAR
0.00 m
26.84 m
Taxiway centreline light
EL-TAXICL
0.00 m
26.21 m
Taxiway edge light
EL-TAXIWAY EDGE
0.07 m !
26.02 m
Taxiway edge light
EL-TAXIWAY EDGE
0.00 m
24.20 m
Stop bar light
EL-STOPBAR
0.00 m
23.28 m
Taxiway centreline light
EL-TAXICL
0.00 m
22.49 m
Taxiway centreline light
EL-TAXICL
0.03 m
22.42 m
Taxiway centreline light
EL-TAXICL
0.00 m
22.33 m
Taxiway centreline light
EL-TAXICL
0.00 m
21.99 m
Taxiway centreline light
EL-TAXICL
0.00 m
21.24 m
Stop bar light
EL-STOPBAR
0.00 m
19.86 m
Taxiway centreline light
EL-TAXICL
0.00 m
19.69 m
Taxiway centreline light
EL-TAXICL
0.00 m
18.29 m
Stop bar light
EL-STOPBAR
0.00 m
15.37 m
Stop bar light
EL-STOPBAR
0.00 m
12.96 m
Sign foundation
EL-SGN-FNDTN
0.00 m
12.84 m
Sign foundation
EL-SGN-FNDTN
0.28 m !
12.48 m
Stop bar light
EL-STOPBAR
0.00 m
9.66 m
Stop bar light
EL-STOPBAR
0.00 m
8.85 m
Handhole
CV_HH
0.00 m
2.83 m
Existing transformer handhole
CV_ETRANS HH
2.83 m !
! offset >50 mm — confirm the termination on site
LOC-02 — DERIVED SPUR SCHEDULE
1 transformer-handhole hub(s) · 6 spurs · 142.5 m to lights
Length
Terminates at
Source layer
Offset
41.50 m
Taxiway centreline light
EL-TAXICL
0.00 m
30.30 m
Taxiway centreline light
EL-TAXICL
0.00 m
29.10 m
Taxiway centreline light
EL-TAXICL
0.00 m
21.10 m
Taxiway centreline light
EL-TAXICL
0.00 m
20.52 m
Taxiway centreline light
EL-TAXICL
0.00 m
6.23 m
Handhole
CV_HH
0.00 m
! offset >50 mm — confirm the termination on site
LOC-03 — DERIVED SPUR SCHEDULE
2 transformer-handhole hub(s) · 20 spurs · 412.1 m to lights
Length
Terminates at
Source layer
Offset
31.97 m
Taxiway centreline light
EL-TAXICL
0.00 m
31.13 m
Stop bar light
EL-STOPBAR
0.00 m
29.02 m
Taxiway centreline light
EL-TAXICL
0.00 m
28.16 m
Stop bar light
EL-STOPBAR
0.00 m
27.57 m
Taxiway centreline light
EL-TAXICL
0.00 m
25.99 m
Runway guard light / RRM
EL-RRM
4.99 m !
25.23 m
Stop bar light
EL-STOPBAR
0.00 m
25.07 m
Taxiway centreline light
EL-TAXICL
0.00 m
23.13 m
Taxiway centreline light
EL-TAXICL
0.00 m
22.34 m
Stop bar light
EL-STOPBAR
0.00 m
21.12 m
Taxiway centreline light
EL-TAXICL
0.00 m
20.68 m
Taxiway centreline light
EL-TAXICL
0.07 m !
20.57 m
Taxiway centreline light
EL-TAXICL
0.00 m
20.47 m
Taxiway centreline light
EL-TAXICL
0.00 m
19.24 m
Stop bar light
EL-STOPBAR
0.00 m
16.34 m
Stop bar light
EL-STOPBAR
0.00 m
13.46 m
Stop bar light
EL-STOPBAR
0.00 m
10.65 m
Stop bar light
EL-STOPBAR
0.00 m
7.00 m
Handhole
CV_HH
0.00 m
6.80 m
Handhole
CV_HH
0.00 m
! offset >50 mm — confirm the termination on site
Spur lengths are drawn-geometry branch lengths at a 0.30 m snap tolerance — not proven pulls. topology.json accompanies this deck.

## Slide 8
SHEET 8 — AS-BUILT AGL ASSET SYMBOL SCHEDULE · TWY E (E4–E6) REV P06
HOW TO READ THIS
Circle = light · square = civil chamber · triangle = earthing · filled rectangle = sign foundation. Lights are coloured to the light's own showing: taxiway centreline green, taxiway edge blue, stop bar red, runway guard amber. A dashed outline marks the source drawing's "existing" layer for that family.
Asset type is taken from the source-drawing LAYER, never from the label on the sheet. Assets that carry a Rev P05 works-action marker keep that marker instead of a type symbol — their type is in the ID label and in this schedule. Counts are assets inside each sheet frame.
SYMBOL · ASSET TYPE · SOURCE LAYER · COUNT PER SHEET
Symbol
Asset type
Source drawing layer(s)
LOC-01
LOC-02
LOC-03
Total in frame
TWY CENTRELINE LIGHT
EL-TAXICL
31
9
23
63
TWY EDGE LIGHT
EL-TAXIWAY EDGE
4
—
—
4
STOP BAR LIGHT
EL-STOPBAR
8
—
8
16
RUNWAY GUARD LIGHT / RRM
EL-RRM
6
5
9
20
EXISTING LIGHT BASE (NO FITTING)
EL-EBASE
—
—
4
4
SIGN FOUNDATION
EL-SGN-FNDTN
2
—
2
4
HANDHOLE (HH)
CV_HH
11
2
7
20
TRANSFORMER HANDHOLE (SECONDARY FEED HUB)
CV_ETRANS HH
5
1
2
8
MANHOLE (MH)
CV_MH
2
—
2
4
TRANSFORMER MANHOLE (SEC. FEED)
CV_ETRANS MH
2
—
2
4
EARTHING POINT
CV_GRND
10
3
7
20
EARTHING PIT
CV_GRND PIT
1
1
—
2
TOTAL — 12 asset types
82
21
66
169
Of these, Rev P05 drew no symbol at all for 42 assets on LOC-01, 12 on LOC-02 and 31 on LOC-03 — they are added in Rev P06 from the as-built and are NOT field-verified. asset_census.json accompanies this deck.