## Slide 1
SHOP DRAWINGS — ELECTRICAL / AGL SCOPE
RECTIFICATION OF TWY E BETWEEN E4 & E6 (ZIA)
AGL WORKS AT THREE (3) MILLING LOCATIONS — FIELD CONDITION SCOPE
Document No.
AUH-SK-AGL-TWYE-001 (sheets 1001 / 1002 / 1003) · Revision P08 — FINAL SCOPE OF WORK
Basis of scope
Final scope of work issued 30.07.2026, superseding the Rev P06 / P07 field-sheet quantities. Quantities and locations are taken from the joint field verification of the three milling locations.
Base layer
ADA as-built drawing Z1-Z2-Z3-MTA_SEGMENTATION · ZIA local project grid (metres)
Prepared by
Approved by
Mohammed Faheem — AGL Team Leader, ADB SAFEGATE · Issued 28.07.2026 · Rev P08 issued 30.07.2026
Ragesh Menon — AGL Manager, ADB SAFEGATE
REV P08 IS THE FINAL SCOPE OF WORK. All secondary routes at the three locations are laid by SAW CUT; no duct route remains in the AGL scope. New side-entry shallow bases: Location 1 — 11 No. 8" (9 No. bases cored out: 3 No. 12" + 6 No. 8"; 2 No. 12" bases removed earlier); Location 2 — 1 No. 12" at TCCECH-03/008; Location 3 — 1 No. 12" at TCCECH-03/003, with the remaining 3 No. TCC taking new secondary cable into their existing 12" bases. A further 3 No. fittings at Location 1 (SBC102-02/027, TCCECH-03/035, TCCECH-03/018) take new secondary cable only — no coring — and are protected by a dummy plate during milling. The affected-fitting list moves from 30 No. to 19 No. A saw cut and side-entry base detail sheet is included and is held pending issue of the detail drawing. The technical queries on the existing 4 x 19 mm secondary duct are closed by agreement between the AGL team, the civil team and ADA AGL: saw cut is adopted as an interim arrangement, with permanent duct provision to follow under the South Rehabilitation works. As-built duct geometry, sheet registration and the stated limits of Rev P06 are carried forward unchanged.

## Slide 2
SCOPE OF WORK & SEQUENCE — TWY E (E4–E6) · REV P08 (FINAL SCOPE)
SCOPE OF WORK — SEQUENCE OF AGL ACTIVITIES
PHASE 1 — BEFORE ASPHALT MILLING · AGL ASSET REMOVAL (BEFORE CIVIL WORKS)
R1. Isolate affected circuits; remove affected fittings; core out bases — LOC-01 9 No. (3 No. 12" + 6 No. 8"; 2 No. 12" bases removed earlier); LOC-02 TCCECH-03/008 12"; LOC-03 TCCECH-03/003 12".
R2. RRMs removed and protected (RRM.555, RRM.557, RRM.670) — re-fixed after civil works.
R3. Dummy plates installed on the open bases, and on the 3 No. Location 1 fittings that take secondary cable only (SBC102-02/027, TCCECH-03/035, TCCECH-03/018), for protection during milling and civil works.
PHASE 2 — CIVIL WORKS · ASPHALT MILLING & LAYING (AGL ATTENDANCE)
A1. Where secondary duct or secondary cable is laid by the civil team, a mandrel test is to be carried out on every duct and witnessed by the AGL team BEFORE asphalt laying. Asphalt laying to follow the witnessed mandrel test.
PHASE 3 — AFTER CIVIL WORKS · AGL INSTALLATION
1. AGL installation works to commence only after written confirmation from the civil team that the asphalt curing period is complete.
2. Saw cutting to commence only after the survey points are confirmed in the field by the civil survey team, and not before the saw cut detail drawing is issued. At Rev P08 every secondary route at the three locations is saw cut, and no duct route remains in the AGL scope.
3. Installation of new bases — SIDE-ENTRY SHALLOW BASE: 11 No. 8" at Location 1; 1 No. 12" at Location 2; 1 No. 12" at Location 3 (TCCECH-03/003 — no side-entry provision in existing base). Balance 3 No. TCC at Location 3 and 3 No. at Location 1: existing shallow base maintained, new side-entry cable only, no coring.
4. Laying of new secondary cable through the saw cut — 1 No. 2-core 4 sq.mm cable to each fitting, SBC and TCC alike (7 No. SBC, 12 No. TCC). No joints — full manhole-to-light replacement.
5. Secondary cable termination, insulation resistance and continuity testing.
6. Testing and commissioning at circuit level — covering the affected fittings together with the fittings on the same circuits that fall outside these works, since the series circuits are proved end to end before handover.
7. Final functionality check, then handover to Operations for final inspection and return of the area to operational service.
HOLD POINTS & WITNESS REQUIREMENTS
H1 Curing complete — Civil. Written confirmation of the asphalt curing period before AGL installation works start (Phase 3, Item 1).
H2 Setting-out — Civil survey. Coordinates issued and field points confirmed before coring (Phase 1, R1) and before saw cutting (Phase 3, Item 2).
H3 Mandrel test — AGL witness. Every duct laid by the civil team, before asphalt laying (Item A1).
H4 Functionality check — AGL / Operations. Witnessed before handover (Phase 3, Item 7).
H5 Saw cut detail — AGL / Engineer. Saw cutting to start once the saw cut and side-entry base detail drawing is issued and accepted (Rev P08).
TECHNICAL QUERY — CLOSED BY AGREEMENT (AGL TEAM · CIVIL TEAM · ADA AGL)
Subject: existing 4 x 19 mm secondary duct — cover, reuse and continuity
Field condition: the existing 4 x 19 mm secondary duct bank was exposed at 50 mm milling depth.
Q1. Whether new duct may be re-laid on the existing duct alignment. CLOSED — no duct is re-laid on the existing alignment under this scope; the new secondary cable is laid by saw cut.
Q2. Suitability of the existing duct for reuse. CLOSED — the existing 4 x 19 mm cross-section does not accommodate the new secondary cable, and the existing cables are obsolete and are to be withdrawn. Reuse is not adopted; the duct bank is left in place.
Q3. Transition into the duct in the non-construction area. CLOSED — the civil scope of work covers the milling area only, so a full-stretch duct cannot be delivered under this work. Saw cut is adopted for the full affected length, which removes the transition.
AGREED WAY FORWARD — SAW CUT AS AN INTERIM ARRANGEMENT
The AGL team's original proposal was a full-stretch new secondary duct sized for the new secondary cable, giving a continuous route end to end and minimising saw cutting in the finished pavement.
Agreed position: the matter was raised with the civil team and with ADA AGL. It is agreed that the existing 4 x 19 mm duct cannot accommodate the new secondary cable, and that the civil scope of work covers the milling area only, so a full-stretch duct cannot be delivered under this work. SAW CUT is therefore adopted for every milling-affected asset — agreed by the AGL team (ADB SAFEGATE), the civil team and ADA AGL.
Status: the saw cut route is an INTERIM arrangement. Permanent duct provision is to follow under the South Rehabilitation works, where the saw cut routes are to be replaced with duct to the standard design. Q1, Q2 and Q3 are closed on that basis.
REV P08 — WHAT CHANGED
All secondary routes saw cut at the three locations; no duct route remains in the AGL scope.
New SIDE-ENTRY SHALLOW BASES — LOC-01 11 No. 8" (3 No. 12" + 6 No. 8" cored out, 2 No. 12" removed earlier); LOC-02 and LOC-03 1 No. 12" each.
Affected fittings move from 30 No. to 19 No.: LOC-01 14 (11 with new bases, 3 secondary cable only), LOC-02 1 (TCCECH-03/008), LOC-03 4 (TCC only — 03/003 cored, balance 3 secondary cable only).
Coring: 11 No. in total — LOC-01 9 No. (3 No. 12" + 6 No. 8"); LOC-02 1 No. 12"; LOC-03 1 No. 12".
Technical queries Q1–Q3 on the existing 4 x 19 mm secondary duct are closed by agreement between the AGL team, the civil team and ADA AGL: saw cut is adopted as an interim arrangement, with permanent duct provision under the South Rehabilitation works.
Sequence and hold points apply to the three milling locations (sheets 1001, 1002, 1003). Field condition governs. Where this sequence and a civil programme instruction differ, the AGL Team Leader is to be informed so that the two can be aligned before work proceeds. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 3
AGL INSTALLATION — 5-DAY WORK SCHEDULE · TWY E (E4–E6) · REV P08 (FINAL SCOPE)
DAY 1
SETTING-OUT & SAW CUT START
LOCATION 1 · SHEET 1001
DAY 2
SAW CUT COMPLETE · NEW BASES
LOCATION 1 · SHEET 1001
DAY 3
CABLE, TEST & REINSTATEMENT
LOCATION 1 · SHEET 1001
DAY 4
FULL CYCLE — CUT TO SEALED
LOCATION 3 · SHEET 1003
DAY 5
FULL CYCLE + T&C & HANDOVER
LOCATION 2 · SHEET 1002
FIVE-DAY PROGRAMME — PHASE 3 AGL INSTALLATION
Day | Phase 3 activity | Location | Quantity | Hold point / witness | Output at the end of the shift
1 | Setting-out from the civil survey points — all three locations in one visit | LOC-01 / 02 / 03 | 3 No. locations | H2 — civil survey | Field points confirmed and marked at all three
1 | Saw cutting — first part of the secondary cable route | LOC-01 · 1001 | approx. 150 m | H5 — detail accepted | Half the LOC-01 route cut and covered
2 | Saw cutting — balance of the route | LOC-01 · 1001 | approx. 150 m | H5 — detail accepted | LOC-01 route cut in full
2 | Set the new side-entry shallow bases in the cored positions | LOC-01 · 1001 | 11 No. 8" | — | 11 No. bases set and levelled
3 | Lay new secondary cable through the saw cut — no joints, manhole to light | LOC-01 · 1001 | 14 No. runs | — | LOC-01 cabled
3 | Termination, insulation resistance and continuity testing | LOC-01 · 1001 | 14 No. fittings | — | LOC-01 test records issued
3 | Backfill, sealant and pavement reinstatement of the saw cut | LOC-01 · 1001 | approx. 300 m | Per the awaited detail | LOC-01 cut sealed; cure period started
4 | Saw cutting — full route | LOC-03 · 1003 | approx. 95 m | H5 — detail accepted | LOC-03 route cut
4 | Set 1 No. new base; the balance takes side entry into its existing base | LOC-03 · 1003 | 1 No. 12" + 3 No. | — | Bases ready to receive cable
4 | Cable, termination, insulation resistance and continuity testing | LOC-03 · 1003 | 4 No. runs | — | LOC-03 test records issued
4 | Reinstatement of the cut; re-fix RRM.557 and RRM.670 | LOC-03 · 1003 | approx. 95 m · 2 No. RRM | Per the awaited detail | LOC-03 sealed; RRMs re-fixed
5 | Saw cut, new base, cable, termination and testing | LOC-02 · 1002 | approx. 24 m · 1 No. 12" | H5 — detail accepted | LOC-02 complete and tested
5 | Reinstatement of the cut; re-fix RRM.555 | LOC-02 · 1002 | approx. 24 m · 1 No. RRM | Per the awaited detail | LOC-02 sealed; RRM re-fixed
5 | Testing and commissioning at circuit level — affected and unaffected fittings alike | LOC-01 / 02 / 03 | 4 No. circuits | — | Circuits energised and proved end to end
5 | Final functionality check, then handover to Operations | LOC-01 / 02 / 03 | 19 No. fittings | H4 — AGL / Operations | Area returned to operational service
HOLD POINTS GOVERNING THE PROGRAMME
H1 Curing complete — Civil. Written confirmation of the asphalt curing period. Required before Day 1 starts.
H5 Saw cut detail — AGL / Engineer. Detail drawing issued and accepted. Required before any cutting on Day 1.
H2 Setting-out — Civil survey. Coordinates issued and field points confirmed in the field. Day 1.
H4 Functionality check — AGL / Operations. Witnessed before handover. Day 5.
H3 (mandrel test) sits in Phase 2 civil works and falls outside these five days.
BASIS, ASSUMPTIONS & INDICATIVE RESOURCES
Covers Phase 3 AGL installation only. Phase 1 asset removal and coring is recorded complete (site record 23.07.2026); Phase 2 civil attendance sits outside these five days.
The three locations are worked one front at a time — LOC-01 over Days 1–3, LOC-03 on Day 4, LOC-02 on Day 5 — so each is cut, cabled, tested and sealed before the next is opened. Days are allocated to the work each location carries: 14 No. fittings and approx. 300 m of cut at LOC-01, 4 No. and approx. 95 m at LOC-03, 1 No. and approx. 24 m at LOC-02.
Only two items span all three locations: the setting-out on Day 1, taken in one survey visit, and the circuit testing and commissioning on Day 5, which cannot complete until every location is cabled because the circuits run through all three.
One day = one approved working shift under the AWAN / PTW. The sequence holds for a day or a night closure; shift hours to be set against the approved airside window.
The five days run consecutively from the release of H1 and H5. Neither is released at the date of this revision.
Saw cut lengths scaled from sheets 1001–1003 — approx. 300 m, 24 m and 95 m, approx. 420 m in total. For programme only; confirm on site.
Sealant cure time before the area returns to operational service is per the awaited saw cut detail. If it exceeds the Day 5 shift, handover moves to the following shift.
Indicative resourcing per shift: 1 No. AGL supervisor, 4 No. AGL technicians, 2 No. saw cut operatives, 1 No. safety banksman; survey attendance Day 1, Operations attendance Day 5. To be confirmed against the approved AWAN.
Programme for the AGL installation phase. It is issued for planning and for co-ordination with the civil programme; it is not a construction instruction until the hold points above are released. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 4
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 1 · DWG NO AUH-SK-AGL-TWYE-001-1001 REV P08
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
RRM.76
RRM.282
TCCECH.04.018
RRM.539
RRM.540
RRM.541
RRM.636
TCC103.12.019
TCC103.11.019
TCC103.11.020
TEC102.02.047
TEC102.02.048
TEC102.02.049
HH.E6.033
TCCECH.03.017
TCCECH.04.016
TCCECH.03.016
TCCECH.04.015
TCCECH.03.015
SBC102.02.027
TCC103.11.027
TCCECH.03.038
TCCECH.04.037
TCCECH.03.039
TCCECH.04.038
TCCECH.04.019
TCCECH.03.020
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
HH.E6.038
HH.E6.037
HH.E6.036
HH.E6.035
HH.E6.040
HH.E6.041
HH.E6.042
HH.E6.034
HH.E6.032
HH.E6.039
P6.009
P6.038
MH.E.024
MH.E.014
X_CV_STH_PITS &.23918
SGC102.02.017
SGC102.02.016
TEC102.02.050
SBC102-02/024
SBC102-01/027
SBC102-02/025
SBC102-01/028
SBC102-02/026
SBC102-01/029
TCCECH-04/034
TCCECH-03/036
TCCECH-04/035
TCCECH-03/037
TCCECH-04/036
SBC102-02/027
TCCECH-03/035
TCCECH-03/018
SBC102-01/026
LOCATION 1 — 1001 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — 14 No. FITTINGS AFFECTED, ALL ROUTES SAW CUT
CORE OUT 3 No. 12" + 6 No. 8" (9 No. cored); 2 No. 12" bases removed earlier — INSTALL 11 No. 8" SIDE-ENTRY SHALLOW BASE + NEW CABLE.
• SBC (6 No.): SBC102-02/024, 01/027, 02/025, 01/028, 02/026, 01/029
• TCC (5 No.): TCCECH-04/034, 03/036, 04/035, 03/037, 04/036
ROUTE: SAW CUT throughout — the Rev P06/P07 via-duct routes become saw cut secondary cable laying at Rev P08. Saw cut detail per the SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL sheet; detail drawing to be issued.
SECONDARY CABLE ONLY — 3 No.: SBC102-02/027, TCCECH-03/035, TCCECH-03/018. New saw cut, NO CORING; existing base kept and protected by a dummy plate during milling.
FIELD VERIFIED NOT AFFECTED: SBC102-01/026 (no works)
TCC103 FITTINGS NOT IN THE FIELD SCOPE — SHOWN AS EXISTING ONLY
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
SITE RECORD — 23.07.2026: 9 No. bases cored out, 2 No. removed. 30.07.2026: preparing installation, all 11 No. new bases 8".
Rev P08 supersedes the Rev P06/P07 quantities. Superseded = no works under this revision; it is not a field verification that the asset is unaffected.
RED AGL WORKS AREA = the Rev P05 field-condition milling extent, unchanged at Rev P08 — the civil milling limit.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres. The EPSG:32640 reference carried on Rev P06 is withdrawn — no surveyed local-to-UTM transform is held, so no UTM coordinate is to be taken from this sheet.
2. AGL works area (red) is the Rev P05 field-condition milling extent, unchanged at Rev P08 — it is the civil milling limit and is not derived from the affected-asset positions.
3. Duct / ductbank / conduit / saw cut lines are as-built geometry lifted from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf. The source layer name carries the duct size and way-count.
4. Ducts are drawn as the separate segments they are in the source. Continuity is not proven — a continuous pull length is not to be taken from this sheet.
5. Isolate, lock out and prove dead all listed circuits at the CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit approximately 2.1–2.3 m off the source insertion point; set out civil features from survey.
7. Centreline and stop bar are taken from the as-built TCC / SBC fittings. Taxiway edge is indicative at 23 m — to be confirmed on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type is taken from the source layer, not from the label.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 8" SIDE-ENTRY BASE (SAW CUT)
SECONDARY CABLE ONLY — NO CORING (DUMMY PLATE)
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
RUNWAY GUARD LIGHT / RRM (6)
HANDHOLE (HH) (11)
TRANSFORMER HH (SEC. FEED HUB) (5)
CORE OUT 8" — NEW 8" SIDE-ENTRY BASE (SAW CUT)
NEW SAW CUT — SECONDARY CABLE (REV P08)
AS-BUILT AGL ASSETS
AGL WORKS AREA — FIELD CONDITION (425.3 m² TOTAL)
Field condition governs. Quantities are per the Rev P08 final scope of work (30.07.2026) and are for check by the Engineer. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 5
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 2 · DWG NO AUH-SK-AGL-TWYE-001-1002 REV P08
P2.002
RRM.545
RRM.546
RRM.554
RRM.556
X_CV_STH_PITS &.24043
TCCECH.03.010
TCCECH.04.009
TCCECH.04.007
TCCECH.03.007
TCCECH.04.006
TCCECH.03.006
TCCECH.03.008
TCCECH.04.008
TCCECH.03.009
P2.002
HH.E.055
HH.E.056
TCCECH-03/007
TCCECH-04/007
TCCECH-03/008
TCCECH-04/008
TCCECH-03/009
RRM.555
LOCATION 2 — 1002 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — 1 No. FITTING AFFECTED, SAW CUT
CORE OUT 12" EXISTING SHALLOW BASE + INSTALL NEW 12" SIDE-ENTRY SHALLOW BASE + NEW CABLE: 1 No.
• TCCECH-03/008 — 12" coring of the existing shallow base; new 12" side-entry base installed; secondary cable via SAW CUT. Saw cut detail per the SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL sheet; detail drawing to be issued.
DUCTS: the remaining ducts in frame are not affected during milling — no duct works at Location 2.
NOT IN THE REV P08 SCOPE — no works: TCCECH-03/007, 04/007, 04/008, 03/009
Rev P06/P07 carried all 5 No. as new-secondary-cable-only via duct; the final scope names 03/008 only.
RRM.555 (0.41 m from the cut): REMOVE / PROTECT BEFORE SAW CUT, RE-FIX AFTER PAVING
ISOLATE CIRCUITS: TCCECH.03, TCCECH.04
Rev P08 supersedes the Rev P06/P07 quantities. Superseded = no works under this revision; it is not a field verification that the asset is unaffected.
RED AGL WORKS AREA = the Rev P05 field-condition milling extent, unchanged at Rev P08 — the civil milling limit.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres. The EPSG:32640 reference carried on Rev P06 is withdrawn — no surveyed local-to-UTM transform is held, so no UTM coordinate is to be taken from this sheet.
2. AGL works area (red) is the Rev P05 field-condition milling extent, unchanged at Rev P08 — it is the civil milling limit and is not derived from the affected-asset positions.
3. Duct / ductbank / conduit / saw cut lines are as-built geometry lifted from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf. The source layer name carries the duct size and way-count.
4. Ducts are drawn as the separate segments they are in the source. Continuity is not proven — a continuous pull length is not to be taken from this sheet.
5. Isolate, lock out and prove dead all listed circuits at the CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit approximately 2.1–2.3 m off the source insertion point; set out civil features from survey.
7. Centreline and stop bar are taken from the as-built TCC / SBC fittings. Taxiway edge is indicative at 23 m — to be confirmed on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type is taken from the source layer, not from the label.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 12" SIDE-ENTRY BASE (SAW CUT)
RRM — REMOVE / PROTECT / RE-FIX
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
RUNWAY GUARD LIGHT / RRM (5)
HANDHOLE (HH) (2)
TRANSFORMER HH (SEC. FEED HUB) (1)
NEW SAW CUT — SECONDARY CABLE (REV P08)
AGL WORKS AREA — FIELD CONDITION (257.1 m² TOTAL)
Field condition governs. Quantities are per the Rev P08 final scope of work (30.07.2026) and are for check by the Engineer. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 6
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 3 · DWG NO AUH-SK-AGL-TWYE-001-1003 REV P08
P4.037
HH.E.058
RRM.283
P4.036.399
TCCECH.04.005
TCCECH.04.004
RRM.547
RRM.548
RRM.558
RRM.559
RRM.655
RRM.669
HH.E.144
TCCECH.03.006
TCCECH.03.004
TCCECH.04.003
TCCECH.03.003
TCCECH.04.002
TCCECH.03.005
TCCECH.05.034
TCCECH.05.033
TCCECH.06.035
TCCECH.06.036
EL.EBASE.13328
EL.EBASE.13329
EL.EBASE.13330
EL.EBASE.13331
TCCECH.03.002
SBC102.01.040
SBC102.02.037
SBC102.01.041
SBC102.02.038
TCC102.01.052
TCC102.02.050
TCCECH.03.001
TCCECH.05.016
TCCECH.05.017
TCCECH.06.019
TCCECH.06.017
TCCECH.06.018
TCCECH.04.001
TCCECH.05.018
P4.037
P4.039
HH.E.057
HH.E.061
HH.E.060
HH.E4.010
HH.E.058
HH.E.059
P4.041
MH.E.015
MH.E.023
SGC102.02.015
SGC102.02.014
SBC102-01/038
SBC102-01/039
SBC102-02/035
SBC102-02/036
SBC102-01/040
SBC102-01/041
SBC102-02/037
SBC102-02/038
TCCECH-03/002
TCCECH-04/002
TCCECH-03/003
TCCECH-04/003
RRM.557
RRM.670
LOCATION 3 — 1003 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — 4 No. TCC, SAW CUT + NEW CABLE; CORE OUT 12" AT 1 No. ONLY
• TCCECH-03/003 — CORE OUT 12" + INSTALL NEW 12" SIDE-ENTRY SHALLOW BASE (no side-entry provision in the existing base).
• TCCECH-03/002, 04/002, 04/003 — SECONDARY CABLE ONLY; the existing 12" shallow base accommodates side entry — NO CORING.
ROUTE: SAW CUT — these 4 No. were carried as via-duct on Rev P06/P07. Saw cut detail per the SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL sheet; detail drawing to be issued.
NOT IN THE REV P08 SCOPE — no works, 8 No. SBC:
• SBC102-01/038, 01/039, 02/035, 02/036 (EP7 stop bar — was saw cut, base protect)
• SBC102-01/040, 01/041, 02/037, 02/038 (was new cable only, via duct)
RRM.557 (0.07 m — treat as within the works) and RRM.670: REMOVE / PROTECT / RE-FIX
ISOLATE CIRCUITS: TCCECH.03/.04 — SBC102.01/.02 carries no AGL works here at Rev P08; confirm isolation against the saw cut alignment before works.
Rev P08 supersedes the Rev P06/P07 quantities. Superseded = no works under this revision; it is not a field verification that the asset is unaffected.
RED AGL WORKS AREA = the Rev P05 field-condition milling extent, unchanged at Rev P08 — the civil milling limit.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres. The EPSG:32640 reference carried on Rev P06 is withdrawn — no surveyed local-to-UTM transform is held, so no UTM coordinate is to be taken from this sheet.
2. AGL works area (red) is the Rev P05 field-condition milling extent, unchanged at Rev P08 — it is the civil milling limit and is not derived from the affected-asset positions.
3. Duct / ductbank / conduit / saw cut lines are as-built geometry lifted from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf. The source layer name carries the duct size and way-count.
4. Ducts are drawn as the separate segments they are in the source. Continuity is not proven — a continuous pull length is not to be taken from this sheet.
5. Isolate, lock out and prove dead all listed circuits at the CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit approximately 2.1–2.3 m off the source insertion point; set out civil features from survey.
7. Centreline and stop bar are taken from the as-built TCC / SBC fittings. Taxiway edge is indicative at 23 m — to be confirmed on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type is taken from the source layer, not from the label.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 12" SIDE-ENTRY BASE (SAW CUT)
RRM — REMOVE / PROTECT / RE-FIX
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
RUNWAY GUARD LIGHT / RRM (9)
HANDHOLE (HH) (7)
TRANSFORMER HH (SEC. FEED HUB) (2)
SECONDARY CABLE ONLY — EXISTING BASE (SAW CUT)
NEW SAW CUT — SECONDARY CABLE (REV P08)
AGL WORKS AREA — FIELD CONDITION (676.7 m² TOTAL)
Field condition governs. Quantities are per the Rev P08 final scope of work (30.07.2026) and are for check by the Engineer. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 7
WORKS QUANTITIES — CORING, SAW CUT & SECONDARY CABLE · TWY E (E4–E6) · REV P08
19 No.
AFFECTED FITTINGS
14 · 1 · 4 across LOC-01 / 02 / 03
11 No.
EXISTING BASES CORED OUT
6 @ 8" · 5 @ 12"
13 No.
NEW SIDE-ENTRY BASES
11 @ 8" · 2 @ 12"
approx. 420 m
SAW CUTTING
300 m · 24 m · 95 m
19 No.
SECONDARY CABLE RUNS
no joints — manhole to light
WORKS QUANTITIES BY LOCATION — REV P08 FINAL SCOPE
Location | Affected assets | Core out existing 8" | Core out existing 12" | New coring 8" base | New coring 12" base | Saw cutting | Secondary cable required (2c x 4 sq.mm)
LOC-01 · sheet 1001 | 14 No. | 6 No. | 3 No. † | 11 No. | — | approx. 300 m | 14 No. runs · approx. 300 m
LOC-02 · sheet 1002 | 1 No. | — | 1 No. | — | 1 No. | approx. 24 m | 1 No. run · approx. 24 m
LOC-03 · sheet 1003 | 4 No. | — | 1 No. | — | 1 No. | approx. 95 m | 4 No. runs · approx. 95 m
TOTAL | 19 No. | 6 No. | 5 No. | 11 No. | 2 No. | approx. 420 m | 19 No. runs · approx. 420 m
† A further 2 No. 12" bases at LOC-01 were removed earlier and need no coring out; all 11 No. LOC-01 positions still take a new 8" coring, which is why the core-out and new-coring counts differ.
AFFECTED ASSETS BEHIND THE COUNTS — BY WORKS ACTION
Location | Works action | Assets | Count | New base | Cable route
LOC-01 | Core out existing 8" → new side-entry shallow base | SBC102-02/024, 01/027, 02/025, 01/028, 02/026, 01/029 | 6 No. | 8" | Saw cut
LOC-01 | Core out existing 12" (3 No.) or removed earlier (2 No.) → new base | TCCECH-04/034, 03/036, 04/035, 03/037, 04/036 | 5 No. | 8" | Saw cut
LOC-02 | Core out existing shallow base → new side-entry shallow base | TCCECH-03/008 | 1 No. | 12" | Saw cut
LOC-03 | Core out existing 12" → new side-entry shallow base — no side entry in the existing base | TCCECH-03/003 | 1 No. | 12" | Saw cut
LOC-01 | No coring — secondary cable only; dummy plate protection during milling | SBC102-02/027, TCCECH-03/035, TCCECH-03/018 | 3 No. | existing | Saw cut
LOC-03 | No coring — the existing 12" shallow base takes the new side entry | TCCECH-03/002, 04/002, 04/003 | 3 No. | existing | Saw cut
BASIS OF THE QUANTITIES
Quantities are the Rev P08 final scope of work (30.07.2026) and reconcile with the consolidated field-governed scope sheet and the saw cut & coring schedule.
Core out = removal of the existing shallow base by coring. New coring = the core taken to receive the new side-entry shallow base. The two counts differ at LOC-01 because 2 No. 12" bases were removed earlier, so 11 No. new 8" bases are set against 9 No. cored positions.
6 No. fittings take new secondary cable with no coring — 3 No. at LOC-01 (SBC102-02/027, TCCECH-03/035, TCCECH-03/018), kept under a dummy plate during milling, and 3 No. at LOC-03 whose existing 12" shallow base takes the new side entry. The saw cut routes plotted on sheets 1001 and 1003 already serve them.
Cable per fitting: 1 No. 2-core 4 sq.mm secondary cable to each fitting, SBC and TCC alike — 7 No. SBC and 12 No. TCC, 19 No. runs in total (LOC-01 7 SBC + 7 TCC; LOC-02 1 TCC; LOC-03 4 TCC).
Saw cut lengths are scaled from the Rev P08 saw cut runs on sheets 1001–1003 using the per-sheet drawing scale — approx. 300 m, 24 m and 95 m. For programme and enquiry only; confirm on site before ordering.
EXCLUSIONS & ITEMS TO CONFIRM
Core diameter and core depth for the 8" and 12" corings, and the grout / bedding specification for each, are per the awaited saw cut and side-entry shallow base detail. The figures above are counts, not dimensions.
Saw cut width and depth, and the cover to the new secondary cable, are per the same awaited detail — hold point H5.
Secondary cable figures are route lengths taken off the saw cut alignment. An allowance for terminations, base entry and manhole tails is to be added at ordering and is not included here.
No duct is laid under the AGL scope at Rev P08. Saw cut is adopted as an interim arrangement agreed between the AGL team, the civil team and ADA AGL; permanent duct provision follows under the South Rehabilitation works. The existing 4 x 19 mm secondary duct bank is left in place with its obsolete cables withdrawn.
Testing and commissioning is carried out at circuit level: the affected fittings and the fittings on the same circuits that fall outside these works are all proved before handover. No material is allowed here for those unaffected fittings.
Civil works — milling, asphalt laying and pavement reinstatement outside the AGL saw cut — are excluded.
Quantities are for check by the Engineer and are stated against the Rev P08 final scope of work (30.07.2026). Field condition governs. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 8
CONSOLIDATED FIELD-GOVERNED SCOPE — TWY E (E4–E6) · REV P08 (FINAL SCOPE)
Loc | Asset | Works Action | Route | Remarks
LOC-01 | SBC102-02/024 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/027 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-02/025 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/028 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-02/026 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/029 | CORE OUT 8" → NEW 8" SIDE-ENTRY BASE + NEW CABLE | Sawcut | 8" core out; new side-entry base; full manhole-to-light cable replacement via saw cut
LOC-01 | TCCECH-04/034 | CORE OUT 12" / REMOVED EARLIER → NEW 8" BASE + CABLE | Sawcut | 12" base cored (3 No.) or removed earlier (2 No.); new 8" base; cable via saw cut
LOC-01 | TCCECH-03/036 | CORE OUT 12" / REMOVED EARLIER → NEW 8" BASE + CABLE | Sawcut | 12" base cored (3 No.) or removed earlier (2 No.); new 8" base; cable via saw cut
LOC-01 | TCCECH-04/035 | CORE OUT 12" / REMOVED EARLIER → NEW 8" BASE + CABLE | Sawcut | 12" base cored (3 No.) or removed earlier (2 No.); new 8" base; cable via saw cut
LOC-01 | TCCECH-03/037 | CORE OUT 12" / REMOVED EARLIER → NEW 8" BASE + CABLE | Sawcut | 12" base cored (3 No.) or removed earlier (2 No.); new 8" base; cable via saw cut
LOC-01 | TCCECH-04/036 | CORE OUT 12" / REMOVED EARLIER → NEW 8" BASE + CABLE | Sawcut | 12" base cored (3 No.) or removed earlier (2 No.); new 8" base; cable via saw cut
LOC-01 | SBC102-02/027 | SECONDARY CABLE ONLY — NEW SAW CUT, NO CORING | Sawcut | Existing base kept, no coring; protected by dummy plate during milling; new cable via saw cut
LOC-01 | TCCECH-03/035 | SECONDARY CABLE ONLY — NEW SAW CUT, NO CORING | Sawcut | Existing base kept, no coring; protected by dummy plate during milling; new cable via saw cut
LOC-01 | TCCECH-03/018 | SECONDARY CABLE ONLY — NEW SAW CUT, NO CORING | Sawcut | Existing base kept, no coring; protected by dummy plate during milling; new cable via saw cut
LOC-01 | SBC102-01/026 | NOT AFFECTED | — | Field verified — no works
LOC-02 | TCCECH-03/008 | CORE OUT EXISTING → NEW 12" SIDE-ENTRY BASE + CABLE | Sawcut | Existing shallow base cored out; new 12" side-entry base; full cable replacement via saw cut
LOC-02 | TCCECH-03/007 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-02 | TCCECH-04/007 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-02 | TCCECH-04/008 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-02 | TCCECH-03/009 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-02 | RRM.555 | RRM — REMOVE / PROTECT / RE-FIX | — | Remove and protect before saw cut; re-fix after paving
LOC-03 | TCCECH-03/002 | SECONDARY CABLE ONLY — EXISTING 12" BASE KEPT | Sawcut | Existing 12" base accepts the new side-entry cable — no coring; cable via saw cut
LOC-03 | TCCECH-04/002 | SECONDARY CABLE ONLY — EXISTING 12" BASE KEPT | Sawcut | Existing 12" base accepts the new side-entry cable — no coring; cable via saw cut
LOC-03 | TCCECH-03/003 | CORE OUT 12" → NEW 12" SIDE-ENTRY BASE + CABLE | Sawcut | No side-entry provision in the existing base; 12" core; new 12" base; cable via saw cut
LOC-03 | TCCECH-04/003 | SECONDARY CABLE ONLY — EXISTING 12" BASE KEPT | Sawcut | Existing 12" base accepts the new side-entry cable — no coring; cable via saw cut
LOC-03 | SBC102-01/038 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-01/039 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-02/035 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-02/036 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-01/040 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-01/041 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-02/037 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | SBC102-02/038 | NOT IN THE REV P08 SCOPE | — | Carried in Rev P06/P07; not named in the final scope of work 30.07.2026 — no works at this revision
LOC-03 | RRM.557 | RRM — REMOVE / PROTECT / RE-FIX | — | Remove and protect before saw cut; re-fix after paving
LOC-03 | RRM.670 | RRM — REMOVE / PROTECT / RE-FIX | — | Remove and protect before saw cut; re-fix after paving
Totals (Rev P08 final scope): 19 No. fittings — LOC-01 14 No. (9 No. cored: 3 No. 12" + 6 No. 8"; 2 No. 12" removed earlier; 11 No. new 8" bases; balance 3 No. secondary cable only, no coring); LOC-02 1 No. (12" core, new 12" base); LOC-03 4 No. (12" core at 03/003 only, balance 3 No. secondary cable only) — all new cable via SAW CUT. · Coring 11 No. (6 @ 8" · 5 @ 12") · New side-entry bases 13 No. · 12 No. not in the Rev P08 scope · 3 No. RRM remove / protect / re-fix · 1 No. field verified not affected.
AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 9
SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL — TWY E (E4–E6) · REV P08 · HOLD
DETAIL — HELD FOR ISSUE
SAW CUT & CORING SCHEDULE — REV P08 FINAL SCOPE
SIDE-ENTRY SHALLOW BASE — WHAT THE DETAIL MUST ALSO SHOW
10. Side-entry shallow base — depth, entry height above the base floor, entry bore and the seal at the entry.
11. Core diameter and core depth for 8" and for 12", and the grout / bedding specification for each.
12. At Location 2, the method for coring out the existing shallow base and making good before the new 12" base is set.
13. Setting-out tolerance of the base relative to the as-built fitting position, and the level tolerance to finished pavement.
SAW CUT DETAIL DRAWING TO BE ISSUED
The final scope of work records that the saw cut detail drawing will be provided. It had not been issued at the date of this revision.
Until it is issued and accepted, saw cutting is not to commence — hold point H5.
Location | Fittings | Core | New base | Route | Sheet
LOC-01 | 14 No. (7 SBC · 7 TCC) | 9 No. — 3 @ 12" · 6 @ 8" | 11 No. 8" new; 3 No. existing kept | Saw cut | 1001
LOC-02 | 1 No. (TCCECH-03/008) | 1 No. 12" (existing base) | 1 No. 12" side-entry base | Saw cut | 1002
LOC-03 | 4 No. (TCC only) | 1 No. 12" (TCCECH-03/003) | 1 No. 12" new; 3 No. existing kept | Saw cut | 1003
TOTAL | 19 No. | 11 No. — 6 @ 8" · 5 @ 12" | 13 No. new side-entry bases | Saw cut | —
WHAT THE SAW CUT DETAIL MUST ANSWER BEFORE IT CAN BE BUILT TO
Cut geometry
1. Saw cut width and depth, and the tolerance on each.
2. Minimum cover from finished pavement surface to the top of the new secondary cable.
3. Cut termination at the light base — how the cut meets the side entry, and the radius or chamfer at the entry.
4. Minimum offset from slab joints, existing cuts and the milling edge, and what to do where the cut would run within that offset.
Cable and backfill
5. Cable protection within the cut — sleeve, tape or direct — and its fixing.
6. Backfill and sealant specification, layer by layer, with cure time before the area returns to operational service.
7. Reinstatement of the pavement surface and the finished surface tolerance.
Transition
8. How the saw cut route terminates at the edge of the milling area, where the existing 4 x 19 mm duct continues into the non-construction area. Saw cut for the full affected length is agreed, so no duct transition is made; the detail is to show the termination and the seal at that point.
9. Treatment where the saw cut crosses the existing 4 x 19 mm secondary duct bank exposed at 50 mm milling depth, which is left in place.
Items 8 and 9 are the two that go beyond plain detailing. Item 8 follows from the agreed saw cut arrangement and governs the ends of every run. Item 9 is a physical clash with a duct bank already found in the field at 50 mm. Both are to be resolved in the detail rather than on site.
This sheet is a HOLD. It states what the awaited detail has to resolve and the quantities that depend on it; it does not show a section, because none has been issued yet. Quantities are per the Rev P08 final scope of work (30.07.2026) and are for check by the Engineer. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed Faheem, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager