## Slide 1
SHOP DRAWINGS — ELECTRICAL / AGL SCOPE
RECTIFICATION OF TWY E BETWEEN E4 & E6 (ZIA)
AGL WORKS AT THREE (3) MILLING LOCATIONS — FIELD CONDITION SCOPE
Document No.
AUH-SK-AGL-TWYE-001 (sheets 1001 / 1002 / 1003) · Revision P08 — FINAL SCOPE OF WORK
Basis of scope
Final scope of work issued 30.07.2026 — supersedes the Rev P06 / P07 field-sheet quantities. Field verification sheets: Document_3 (LOC-01) · Second_milling_area rev _1 (LOC-02 / LOC-03).
Base layer
Prepared by
Mohammed — AGL Team Leader, ADB SAFEGATE AGL Team · Issued 28.07.2026 · Rev P08 30.07.2026
REV P08 — the final scope of work. All secondary routes at all three locations are SAW CUT; no duct route remains in the AGL scope. New SIDE-ENTRY SHALLOW BASES: LOC-01 11 No. 8" (9 bases cored out — 3 No. 12" + 6 No. 8" — and 2 No. 12" removed prior); LOC-02 1 No. 12" (cored at TCCECH-03/008); LOC-03 1 No. 12" at TCCECH-03/003 only — balance 3 No. TCC secondary cable only into existing 12" bases. The affected-asset list reduces from 30 to 16. A saw cut and side-entry base detail sheet is added and is held for the detail drawing. The as-built duct geometry, registration and stated limits of Rev P06 are carried forward unchanged.

## Slide 2
SCOPE OF WORK & SEQUENCE — TWY E (E4–E6) · REV P08 (FINAL SCOPE)
SCOPE OF WORK — SEQUENCE OF AGL ACTIVITIES
PHASE 1 — BEFORE ASPHALT MILLING · AGL ASSET REMOVAL (BEFORE CIVIL WORKS)
R1. Isolate affected circuits; remove affected fittings; core out bases — LOC-01 9 No. (3 No. 12" + 6 No. 8"; 2 No. 12" bases removed prior); LOC-02 TCCECH-03/008 12"; LOC-03 TCCECH-03/003 12".
R2. RRMs removed and protected (RRM.555, RRM.557, RRM.670) — re-fixed after civil works.
R3. Dummy plates installed on open bases for protection during milling and civil works.
PHASE 2 — CIVIL WORKS · ASPHALT MILLING & LAYING (AGL ATTENDANCE)
A1. Where secondary duct or secondary cable is laid by the civil team, a mandrel test is to be carried out on every duct and witnessed by the AGL team BEFORE asphalt laying. No asphalt to be laid over an unwitnessed duct.
PHASE 3 — AFTER CIVIL WORKS · AGL INSTALLATION
1. AGL installation works to commence only after written confirmation from the civil team that the asphalt curing period is complete.
2. Saw cutting to commence only after the survey points are confirmed in the field by the civil survey team, and not before the saw cut detail drawing is issued. At Rev P08 EVERY secondary route at all three locations is saw cut — no duct route remains in the AGL scope.
3. Installation of new bases — SIDE-ENTRY SHALLOW BASE: 11 No. 8" at Location 1; 1 No. 12" at Location 2; 1 No. 12" at Location 3 (TCCECH-03/003 — no side-entry provision in existing base). Balance 3 No. TCC at Location 3: existing 12" shallow base maintained, new side-entry cable only.
4. Laying of new secondary cable through the saw cut. No joints — full manhole-to-light replacement.
5. Secondary cable termination, insulation resistance and continuity testing.
6. Testing and commissioning of all affected circuits.
7. Final functionality check, then handover to Operations for final inspection and return of the area to operational service.
HOLD POINTS & WITNESS REQUIREMENTS
H2 Curing complete — Civil. Written confirmation of the asphalt curing period before AGL installation works start (Phase 3, Item 1).
H3 Setting-out — Civil survey. Coordinates issued and field points confirmed before coring (Phase 1, R1) and before saw cutting (Phase 3, Item 2).
H4 Mandrel test — AGL witness. Every duct laid by the civil team, before asphalt laying (Item A1).
H5 Functionality check — AGL / Operations. Witnessed before handover (Phase 3, Item 7).
H6 Saw cut detail — AGL / Engineer. No saw cutting before the saw cut and side-entry base detail drawing is issued and accepted (Rev P08).
TECHNICAL QUERY — CONFIRMATION REQUIRED (NOT A CONSTRUCTION INSTRUCTION)
Subject: existing 4 x 110 mm secondary duct — cover, reuse and continuity
Field condition: the existing 4 x 110 mm secondary duct bank was exposed at 50 mm milling depth.
Q1. Confirmation required from the civil team before any duct is re-laid on the existing duct alignment.
Q2. The existing duct cannot be reused for the new secondary cable. The existing cables are obsolete and are to be withdrawn, and the existing duct cross-section will not accommodate the new secondary cable.
Q3. If new duct sized for the new secondary cable is laid within the construction area, confirmation is required from Civil on how the transition into the duct in the non-construction area is to be made. The same condition is expected over the full length, which would otherwise require saw cutting for the full length.
AGL TEAM PROPOSAL
Lay a full-stretch new secondary duct sized to accommodate the new secondary cable, giving a continuous route end to end and minimising saw cutting in the finished pavement.
Status at Rev P08: NOT ADOPTED. The final scope of work issued 30.07.2026 adopts SAW CUT for every secondary route at all three locations, which answers Q3 — the full length is saw cut and no new duct is laid under the AGL scope.
Q1 and Q2 remain OPEN on the existing 4 x 110 mm duct bank: whether it is to be left in place, and confirmation that the obsolete cables are withdrawn. To be raised under RFI AUH-WP-AGL-TWYE-001. Not a construction instruction until answered.
REV P08 — WHAT CHANGED
All secondary routes saw cut at all three locations; no duct route remains in the AGL scope.
New SIDE-ENTRY SHALLOW BASES — LOC-01 11 No. 8" (3 No. 12" + 6 No. 8" cored out, 2 No. 12" removed prior); LOC-02 and LOC-03 1 No. 12" each.
Affected fittings reduce from 30 to 16: LOC-01 11, LOC-02 1 (TCCECH-03/008), LOC-03 4 (TCC only — 03/003 cored, balance 3 secondary cable only).
Coring applies at all three locations: LOC-01 mixed 12"/8" (9 cored); LOC-02 and LOC-03 one 12" core each.
Sequence and hold points apply to all three milling locations (sheets 1001, 1002, 1003). Field condition governs. Where this sequence conflicts with a civil programme instruction, the AGL Team Leader is to be notified before work proceeds. · AUH-SK-AGL-TWYE-001 REV P08 (FINAL SCOPE) · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager

## Slide 3
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 1 · DWG NO AUH-SK-AGL-TWYE-001-1001 REV P08
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
AGL WORKS AREA — FIELD CONDITION (425.3 m² TOTAL)
RRM.76
RRM.282
TCCECH.04.018
RRM.539
RRM.540
RRM.541
RRM.636
TCC103.12.019
TCC103.11.019
TCC103.11.020
TEC102.02.047
TEC102.02.048
TEC102.02.049
HH.E6.033
TCCECH.03.017
TCCECH.04.016
TCCECH.03.016
TCCECH.04.015
TCCECH.03.015
SBC102.02.027
TCC103.11.027
TCCECH.03.038
TCCECH.04.037
TCCECH.03.039
TCCECH.04.038
TCCECH.04.019
TCCECH.03.020
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
HH.E6.038
HH.E6.037
HH.E6.036
HH.E6.035
HH.E6.040
HH.E6.041
HH.E6.042
HH.E6.034
HH.E6.032
HH.E6.039
P6.009
P6.038
MH.E.024
MH.E.014
X_CV_STH_PITS &.23918
SGC102.02.017
SGC102.02.016
TEC102.02.050
SBC102-02/024
SBC102-01/027
SBC102-02/025
SBC102-01/028
SBC102-02/026
SBC102-01/029
TCCECH-04/034
TCCECH-03/036
TCCECH-04/035
TCCECH-03/037
TCCECH-04/036
SBC102-02/027
TCCECH-03/035
TCCECH-03/018
SBC102-01/026
LOCATION 1 — 1001 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — 11 FITTINGS AFFECTED, ALL ROUTES SAW CUT
CORE OUT 3 No. 12" + 6 No. 8" (9 No. cored); 2 No. 12" bases REMOVED PRIOR — INSTALL 11 No. 8" SIDE-ENTRY SHALLOW BASE + NEW CABLE.
• SBC (6): SBC102-02/024, 01/027, 02/025, 01/028, 02/026, 01/029
• TCC (5): TCCECH-04/034, 03/036, 04/035, 03/037, 04/036
ROUTE: SAW CUT throughout — all Rev P06/P07 VIA DUCT routes change to saw cut secondary cable laying at P08.
Saw cut detail per sheet SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL — detail drawing to be issued.
REMOVED FROM SCOPE AT REV P08 — no works: SBC102-02/027, TCCECH-03/035, TCCECH-03/018
FIELD VERIFIED NOT AFFECTED: SBC102-01/026 (no works)
TCC103 FITTINGS NOT IN FIELD SCOPE — SHOWN AS EXISTING ONLY
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
SITE RECORD 23.07.2026: 9 cored + 2 removals worked. 30.07.2026: PREPARING INSTALLATION — ALL 11 NEW BASES 8".
REV P08 SUPERSEDES the Rev P06/P07 quantities. SUPERSEDED = no works; NOT a field verification that the asset is unaffected.
RED AGL WORKS AREA = Rev P05 field-condition milling extent, UNCHANGED at P08 — the civil milling limit, not a hull of the affected assets.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition — the Rev P05 milling extent, UNCHANGED at Rev P08. Coring at P08: LOC-01 3 No. 12" + 6 No. 8" cored, 11 No. 8" side-entry bases installed; LOC-02 12" at TCCECH-03/008; LOC-03 12" at TCCECH-03/003 only — balance 3 No. TCC secondary cable only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 8" SIDE-ENTRY BASE (SAWCUT)
ONLY SECONDARY CABLE AFFECTED (SAWCUT)
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
RUNWAY GUARD LIGHT / RRM (6)
HANDHOLE (HH) (11)
TRANSFORMER HH (SEC. FEED HUB) (5)
DUMMY PLATE
RRM — REMOVE / PROTECT / RE-FIX
CORE OUT 8" — NEW 8" SIDE-ENTRY BASE (SAWCUT)
NEW SAW CUT — SECONDARY CABLE (REV P08)
AS-BUILT AGL ASSETS

## Slide 4
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 2 · DWG NO AUH-SK-AGL-TWYE-001-1002 REV P08
P2.002
RRM.545
RRM.546
RRM.554
RRM.556
X_CV_STH_PITS &.24043
TCCECH.03.010
TCCECH.04.009
TCCECH.04.007
TCCECH.03.007
TCCECH.04.006
TCCECH.03.006
TCCECH.03.008
TCCECH.04.008
TCCECH.03.009
P2.002
HH.E.055
HH.E.056
TCCECH-03/007
TCCECH-04/007
TCCECH-03/008
TCCECH-04/008
TCCECH-03/009
RRM.555
LOCATION 2 — 1002 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — ONE FITTING AFFECTED, SAW CUT
CORE OUT 12" EXISTING SHALLOW BASE + INSTALL NEW 12" SIDE-ENTRY SHALLOW BASE + NEW CABLE: 1 No.
• TCCECH-03/008 — 12" coring of existing shallow base; new 12" side-entry base installed; secondary cable via SAW CUT.
Saw cut detail per sheet SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL — detail drawing to be issued. DUCTS: remaining ducts in frame NOT AFFECTED during milling — no duct works at LOC-02.
REMOVED FROM SCOPE AT REV P08 — no works: TCCECH-03/007, 04/007, 04/008, 03/009
Rev P06/P07 carried all 5 No. as new-secondary-cable-only via duct. The final scope names 03/008 only.
RRM.555 (0.41 m from cut): REMOVE / PROTECT BEFORE SAWCUT, RE-FIX AFTER PAVING
ISOLATE CIRCUITS: TCCECH.03, TCCECH.04
REV P08 SUPERSEDES the Rev P06/P07 quantities. SUPERSEDED = no works; NOT a field verification that the asset is unaffected.
RED AGL WORKS AREA = Rev P05 field-condition milling extent, UNCHANGED at P08 — the civil milling limit, not a hull of the affected assets.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition — the Rev P05 milling extent, UNCHANGED at Rev P08. Coring at P08: LOC-01 3 No. 12" + 6 No. 8" cored, 11 No. 8" side-entry bases installed; LOC-02 12" at TCCECH-03/008; LOC-03 12" at TCCECH-03/003 only — balance 3 No. TCC secondary cable only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 12" SIDE-ENTRY BASE (SAWCUT)
RRM — REMOVE / PROTECT / RE-FIX
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
RUNWAY GUARD LIGHT / RRM (5)
HANDHOLE (HH) (2)
TRANSFORMER HH (SEC. FEED HUB) (1)
ONLY SECONDARY CABLE AFFECTED (SAWCUT)
DUMMY PLATE
CORE OUT 8" — NEW 8" SIDE-ENTRY BASE (SAWCUT)
NEW SAW CUT — SECONDARY CABLE (REV P08)

## Slide 5
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 3 · DWG NO AUH-SK-AGL-TWYE-001-1003 REV P08
P4.037
HH.E.058
AGL WORKS AREA — FIELD CONDITION (676.7 m² TOTAL)
RRM.283
P4.036.399
TCCECH.04.005
TCCECH.04.004
RRM.547
RRM.548
RRM.558
RRM.559
RRM.655
RRM.669
HH.E.144
TCCECH.03.006
TCCECH.03.004
TCCECH.04.003
TCCECH.03.003
TCCECH.04.002
TCCECH.03.005
TCCECH.05.034
TCCECH.05.033
TCCECH.06.035
TCCECH.06.036
EL.EBASE.13328
EL.EBASE.13329
EL.EBASE.13330
EL.EBASE.13331
TCCECH.03.002
SBC102.01.040
SBC102.02.037
SBC102.01.041
SBC102.02.038
TCC102.01.052
TCC102.02.050
TCCECH.03.001
TCCECH.05.016
TCCECH.05.017
TCCECH.06.019
TCCECH.06.017
TCCECH.06.018
TCCECH.04.001
TCCECH.05.018
P4.037
P4.039
HH.E.057
HH.E.061
HH.E.060
HH.E4.010
HH.E.058
HH.E.059
P4.041
MH.E.015
MH.E.023
SGC102.02.015
SGC102.02.014
SBC102-01/038
SBC102-01/039
SBC102-02/035
SBC102-02/036
SBC102-01/040
SBC102-01/041
SBC102-02/037
SBC102-02/038
TCCECH-03/002
TCCECH-04/002
TCCECH-03/003
TCCECH-04/003
RRM.557
RRM.670
LOCATION 3 — 1003 · REV P08 (FINAL SCOPE)
FINAL SCOPE OF WORK 30.07.2026 (supersedes the Rev P06/P07 quantities) — FIELD CONDITION GOVERNS
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
FINAL SCOPE (REV P08) — 4 No. TCC, SAW CUT + NEW CABLE; CORE OUT 12" AT 1 No. ONLY:
• TCCECH-03/003 — CORE OUT 12" + INSTALL NEW 12" SIDE-ENTRY SHALLOW BASE (no side-entry provision in existing base). • TCCECH-03/002, 04/002, 04/003 — SECONDARY CABLE ONLY; existing 12" shallow base accommodates side entry — NO CORING.
ROUTE: SAW CUT — these 4 No. were carried as VIA DUCT on Rev P06/P07.
Saw cut detail per sheet SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL — detail drawing to be issued.
REMOVED FROM SCOPE AT REV P08 — no works, 8 No. SBC:
• SBC102-01/038, 01/039, 02/035, 02/036 (EP7 STOP BAR — was sawcut, base protect)
• SBC102-01/040, 01/041, 02/037, 02/038 (was new cable only, via duct)
RRM.557 (0.07 m — treat as within works) & RRM.670: REMOVE / PROTECT / RE-FIX
ISOLATE CIRCUITS: TCCECH.03/.04 — SBC102.01/.02 carries no AGL works here at P08;
confirm isolation against the saw cut alignment before works.
REV P08 SUPERSEDES the Rev P06/P07 quantities. SUPERSEDED = no works; NOT a field verification that the asset is unaffected.
RED AGL WORKS AREA = Rev P05 field-condition milling extent, UNCHANGED at P08 — the civil milling limit, not a hull of the affected assets.
GENERAL NOTES
1. Positions plotted are ZIA LOCAL PROJECT GRID metres — NOT UTM 40N. The Rev P06 "EPSG:32640" label was wrong; no surveyed local-to-UTM transform exists. Do not issue a UTM coordinate from this sheet.
2. AGL works area (red) per field condition — the Rev P05 milling extent, UNCHANGED at Rev P08. Coring at P08: LOC-01 3 No. 12" + 6 No. 8" cored, 11 No. 8" side-entry bases installed; LOC-02 12" at TCCECH-03/008; LOC-03 12" at TCCECH-03/003 only — balance 3 No. TCC secondary cable only.
3. Duct / ductbank / conduit / sawcut lines are REAL as-built geometry from ADA drawing Z1-Z2-Z3-MTA_SEGMENTATION.dxf — not light-to-nearest-pit construction lines. Layer name carries size and way-count; see sheet 6.
4. Ducts are drawn as the separate segments they are in the source. Continuity NOT proven — do not take a continuous pull length off this sheet.
5. Isolate, lock out & prove dead all listed circuits at CCR under permit before cutting, coring or excavation.
6. HH / MH / transformer-pit / RRM symbols sit ~2.1-2.3 m off the source insertion point (sheet 6) — set out civil features from survey.
7. Centerline & stop bar from as-built TCC / SBC fittings. Edge indicative 23 m — confirm on site.
8. Every asset in frame carries its own as-built symbol, legended right. Type comes from the source layer, not the label. Assets with a works-action marker keep that marker.
LEGEND — THIS SHEET
CORE OUT 12" — NEW 12" SIDE-ENTRY BASE (SAWCUT)
RRM — REMOVE / PROTECT / RE-FIX
SECONDARY CABLE — SAW CUT ROUTE (REV P08)
AGL WORKS AREA (GOVERNING)
WORKS ACTIONS & LINEWORK
AS-BUILT AGL ASSETS
RUNWAY GUARD LIGHT / RRM (9)
HANDHOLE (HH) (7)
TRANSFORMER HH (SEC. FEED HUB) (2)
ONLY SECONDARY CABLE AFFECTED (SAWCUT)
DUMMY PLATE
CORE OUT 8" — NEW 8" SIDE-ENTRY BASE (SAWCUT)
NEW SAW CUT — SECONDARY CABLE (REV P08)

## Slide 6
CONSOLIDATED FIELD-GOVERNED SCOPE — TWY E (E4–E6) · REV P08 (FINAL SCOPE)
Loc | Asset | Works Action | Route | Remarks
LOC-01 | SBC102-02/024 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/027 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-02/025 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/028 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-02/026 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | SBC102-01/029 | CORE OUT 8" + NEW SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | 8" core out; new side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-01 | TCCECH-04/034 | CORE OUT 12" / REMOVED PRIOR — NEW 8" BASE + NEW CABLE | Sawcut | 12" base cored (3 No.) or removed prior (2 No.); new 8" base; cable replaced via saw cut
LOC-01 | TCCECH-03/036 | CORE OUT 12" / REMOVED PRIOR — NEW 8" BASE + NEW CABLE | Sawcut | 12" base cored (3 No.) or removed prior (2 No.); new 8" base; cable replaced via saw cut
LOC-01 | TCCECH-04/035 | CORE OUT 12" / REMOVED PRIOR — NEW 8" BASE + NEW CABLE | Sawcut | 12" base cored (3 No.) or removed prior (2 No.); new 8" base; cable replaced via saw cut
LOC-01 | TCCECH-03/037 | CORE OUT 12" / REMOVED PRIOR — NEW 8" BASE + NEW CABLE | Sawcut | 12" base cored (3 No.) or removed prior (2 No.); new 8" base; cable replaced via saw cut
LOC-01 | TCCECH-04/036 | CORE OUT 12" / REMOVED PRIOR — NEW 8" BASE + NEW CABLE | Sawcut | 12" base cored (3 No.) or removed prior (2 No.); new 8" base; cable replaced via saw cut
LOC-01 | SBC102-02/027 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-01 | TCCECH-03/035 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-01 | TCCECH-03/018 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-01 | SBC102-01/026 | NOT AFFECTED | — | Field verified — no works
LOC-02 | TCCECH-03/008 | CORE OUT EXISTING BASE + NEW 12" SIDE-ENTRY SHALLOW BASE + NEW CABLE | Sawcut | Existing shallow base cored out; new 12" side-entry shallow base; full manhole-to-light cable replacement via saw cut
LOC-02 | TCCECH-03/007 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-02 | TCCECH-04/007 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-02 | TCCECH-04/008 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-02 | TCCECH-03/009 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-02 | RRM.555 | RRM REMOVE / PROTECT | — | Remove / protect before saw cut, re-fix after paving
LOC-03 | TCCECH-03/002 | SECONDARY CABLE ONLY — EXISTING 12" BASE MAINTAINED | Sawcut | Existing 12" base accepts new side-entry cable — no coring; cable via saw cut
LOC-03 | TCCECH-04/002 | SECONDARY CABLE ONLY — EXISTING 12" BASE MAINTAINED | Sawcut | Existing 12" base accepts new side-entry cable — no coring; cable via saw cut
LOC-03 | TCCECH-03/003 | CORE OUT 12" + NEW 12" SIDE-ENTRY BASE + NEW CABLE | Sawcut | No side-entry provision in existing base; 12" core; new 12" base; cable via saw cut
LOC-03 | TCCECH-04/003 | SECONDARY CABLE ONLY — EXISTING 12" BASE MAINTAINED | Sawcut | Existing 12" base accepts new side-entry cable — no coring; cable via saw cut
LOC-03 | SBC102-01/038 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-01/039 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-02/035 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-02/036 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-01/040 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-01/041 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-02/037 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | SBC102-02/038 | NOT IN REV P08 SCOPE | — | In the Rev P06/P07 scope; not named in the final scope of work 30.07.2026. No works. Not a field verification of 'not affected'
LOC-03 | RRM.557 | RRM REMOVE / PROTECT | — | Remove / protect before saw cut, re-fix after paving
LOC-03 | RRM.670 | RRM REMOVE / PROTECT | — | Remove / protect before saw cut, re-fix after paving
Totals (Rev P08 final scope): 16 fittings — LOC-01 11 (9 cored: 3 No. 12" + 6 No. 8"; 2 No. 12" removed prior; 11 No. new 8" bases); LOC-02 1 (12" core, new 12" base); LOC-03 4 (12" core at 03/003 only; balance 3 secondary cable only) — all new cable via SAW CUT. · 15 removed from scope · 3 RRMs remove / protect / re-fix · 1 field verified not affected · Route column reads Sawcut throughout by instruction.

## Slide 7
SAW CUT & SIDE-ENTRY SHALLOW BASE DETAIL — TWY E (E4–E6) · REV P08 · HOLD
DETAIL — HELD FOR ISSUE
SAW CUT & CORING SCHEDULE — REV P08 FINAL SCOPE
SIDE-ENTRY SHALLOW BASE — WHAT THE DETAIL MUST ALSO SHOW
10. Side-entry shallow base — depth, entry height above the base floor, entry bore and the seal at the entry.
11. Core diameter and core depth for 8" and for 12", and the grout / bedding specification for each.
12. At Location 2, the method for coring out the EXISTING shallow base and making good before the new 12" base is set.
13. Setting-out tolerance of the base relative to the as-built fitting position, and the level tolerance to finished pavement.
SAW CUT DETAIL DRAWING TO BE ISSUED
The final scope of work records that the saw cut detail drawing will be provided. It has not been issued at the date of this revision.
Paste the issued detail into this frame and re-issue the sheet. Until it is issued and accepted, NO SAW CUTTING IS TO COMMENCE — hold point H6.
Location | Fittings | Core | New base | Route | Sheet
LOC-01 | 11 (6 SBC · 5 TCC) | 8" | Side-entry shallow base | Saw cut | 1001
LOC-02 | 1 (TCCECH-03/008) | 12" | Side-entry shallow base — existing base cored out | Saw cut | 1002
LOC-03 | 4 (TCC only) | 12" | Side-entry shallow base | Saw cut | 1003
TOTAL | 16 | 11 @ 8" · 5 @ 12" | 16 side-entry shallow bases | Saw cut throughout | —
WHAT THE SAW CUT DETAIL MUST ANSWER BEFORE IT CAN BE BUILT TO
Cut geometry
1. Saw cut width and depth, and the tolerance on each.
2. Minimum cover from finished pavement surface to the top of the new secondary cable.
3. Cut termination at the light base — how the cut meets the side entry, and the radius or chamfer at the entry.
4. Minimum offset from slab joints, existing cuts and the milling edge, and what to do where the cut would run within that offset.
Cable and backfill
5. Cable protection within the cut — sleeve, tape or direct — and its fixing.
6. Backfill and sealant specification, layer by layer, with cure time before the area returns to operational service.
7. Reinstatement of the pavement surface and the finished surface tolerance.
Transition
8. How the saw cut route transitions into the existing duct in the NON-CONSTRUCTION area — this is open technical query Q3 and it governs the ends of every run.
9. Treatment where the saw cut crosses the existing 4 x 110 mm secondary duct bank exposed at 50 mm milling depth.
Items 8 and 9 are the two that are not purely detailing. Item 8 is open technical query Q3 — the transition into the non-construction area was never answered, and every run has two ends. Item 9 is a physical clash with a duct bank the field already found at 50 mm. Neither can be closed out on site.
This sheet is a HOLD. It states what the awaited detail has to resolve and the quantities that depend on it; it does not show a section, because none has been issued. Quantities are per the Rev P08 final scope of work (30.07.2026) and are FOR CHECK by the Engineer. · AUH-SK-AGL-TWYE-001 REV P08 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager