## Slide 1
SHOP DRAWINGS — ELECTRICAL / AGL SCOPE
RECTIFICATION OF TWY E BETWEEN E4 & E6 (ZIA)
AGL WORKS AT THREE (3) MILLING LOCATIONS — FIELD CONDITION SCOPE
Document No.
AUH-SK-AGL-TWYE-001
Base layer
As-built AGL asset survey assets_20260726120533.xlsx — UTM 40N (EPSG:32640)
Prepared by
Approved by
Mohammed — AGL Team Leader, ADB SAFEGATE AGL Team · Issued 28.07.2026
Ragesh Menon — AGL Manager, ADB SAFEGATE AGL Team

## Slide 2
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 1 · DWG NO AUH-SK-AGL-TWYE-001-1001 REV P06
UTM 40N (EPSG:32640) — AS-BUILT POSITIONS · DO NOT SCALE FROM DRAWING
AGL WORKS DEMARCATION — PER FIELD-VERIFIED AFFECTED ASSETS (572.6 m²)
RRM.76
TCCECH.04.018
RRM.540
RRM.541
RRM.636
TCC103.12.019
TCC103.11.019
TCC103.11.020
TEC102.02.047
TEC102.02.048
TEC102.02.049
HH.E6.033
TCCECH.03.017
TCCECH.04.016
TCCECH.03.016
TCCECH.04.015
TCCECH.03.015
TCC103.11.027
TCCECH.03.038
TCCECH.04.037
TCCECH.03.039
TCCECH.04.038
TCCECH.04.019
TCCECH.03.020
X_CV_STH_PITS &.27152
X_CV_STH_PITS &.27153
X_CV_STH_PITS &.27154
X_CV_STH_PITS &.27162
HH.E6.038
HH.E6.037
HH.E6.036
HH.E6.035
HH.E6.041
HH.E6.042
HH.E6.034
HH.E6.032
HH.E6.039
P6.009
P6.038
MH.E.024
MH.E.014
X_CV_STH_PITS &.23918
SGC102.02.017
SGC102.02.016
TEC102.02.050
SBC102-02/024
SBC102-01/027
SBC102-02/025
SBC102-01/028
SBC102-02/026
SBC102-01/029
TCCECH-04/034
TCCECH-03/036
TCCECH-04/035
TCCECH-03/037
TCCECH-04/036
SBC102-02/027
TCCECH-03/035
TCCECH-03/018
SBC102-01/026
LOCATION 1 — 1001 · REV P06 (ISSUED)
SCOPE PER FIELD SHEET Document_3 — FIELD CONDITION GOVERNS
Sheet A3 (420 x 297 mm) · NOT TO SCALE — approx. 1:465 as plotted · UTM 40N · Issued 28.07.2026 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
CORE OUT SHALLOW BASE + NEW CABLE: 11 No.
• VIA DUCT (6): SBC102-02/024, 01/027, 02/025, 01/028, 02/026, 01/029
• VIA SAWCUT (5): TCCECH-04/034, 03/036, 04/035, 03/037, 04/036
NEW SECONDARY CABLE ONLY: 1 No.
• SBC102-02/027 (DUCT)
DUMMY PLATE + NEW CABLE: 6 No. (2 CONFIRMED + 4 PROVISIONAL)
• CONFIRMED: TCCECH-03/035, 03/018 (SAWCUT — bases sound, verify at cut line)
• PROVISIONAL (TCC103): 11/021, 11/126, 12/021, 12/022 — no core-out per field; secondary routes cross the cut, so cable replaced, fitting lifted, dummy plate fitted
FIELD VERIFIED NOT AFFECTED: SBC102-01/026 (no works)
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
SITE RECORD 23.07.2026: 9 cored + 2 reinstatement completed
GENERAL NOTES
1. All asset positions as-built (asset survey assets_20260726120533.xlsx, UTM 40N / EPSG:32640).
2. AGL works demarcation (red) drawn around field-verified affected assets (+2.0 m) — field condition governs.
3. Secondary cables: no joints — full manhole-to-light replacement. Confirm routes vs AGL duct-layout CAD (Rev C) before works.
4. Isolate, lock out & prove dead all listed circuits at CCR under permit before any cutting, coring or excavation.
5. Reinstatement setting-out by civil survey from as-built E/N, checked against adjacent undisturbed fittings before coring.
LEGEND — WORKS ACTIONS (THIS SHEET)
CORE OUT + NEW CABLE (DUCT) — outer red / inner blue
CORE OUT + NEW CABLE (SAWCUT) — outer red / inner orange
NEW SEC. CABLE ONLY (DUCT) — outer blue / inner green
NEW SEC. CABLE ONLY (SAWCUT) — outer orange / inner green
Dummy Plate
EXISTING AGL ASSET (AS-BUILT)
SECONDARY DUCT RUN CROSSING CUT (INDICATIVE)
AGL WORKS DEMARCATION (GOVERNING)
TAXIWAY CENTERLINE (AS-BUILT, THROUGH TCC FITTINGS)
STOP BAR (AS-BUILT, THROUGH SBC FITTINGS)
TWY EDGE / PAVEMENT BOUNDARY (INDICATIVE 23 m — CONFIRM ON SITE)
TCC103-11/021
TCC103-11/126
TCC103-12/021
TCC103-12/022

## Slide 3
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 2 · DWG NO AUH-SK-AGL-TWYE-001-1002 REV P06
UTM 40N (EPSG:32640) — AS-BUILT POSITIONS · DO NOT SCALE FROM DRAWING
AGL WORKS DEMARCATION — PER FIELD-VERIFIED AFFECTED ASSETS (700.3 m²)
RRM.545
RRM.546
RRM.554
RRM.556
X_CV_STH_PITS &.24043
TCCECH.03.010
TCCECH.04.009
TCCECH.04.006
TCCECH.03.006
P2.002
HH.E.055
HH.E.056
TCCECH-03/007
TCCECH-04/007
TCCECH-03/008
TCCECH-04/008
TCCECH-03/009
RRM.555
LOCATION 2 — 1002 · REV P06 (ISSUED)
SCOPE PER FIELD SHEET Second_milling_area rev _1 — FIELD CONDITION GOVERNS
Sheet A3 (420 x 297 mm) · NOT TO SCALE — approx. 1:465 as plotted · UTM 40N · Issued 28.07.2026 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
NEW SECONDARY CABLE ONLY (VIA DUCT): 5 No.
• TCCECH-03/007, 04/007, 03/008, 04/008, 03/009
NO SHALLOW BASES AFFECTED — NO ASSET LIES INSIDE THE MILLING POLYGON HERE
RRM.555 (0.41 m from cut): REMOVE / PROTECT BEFORE SAWCUT, RE-FIX AFTER PAVING
ISOLATE CIRCUITS: TCCECH.03, TCCECH.04
GENERAL NOTES
1. All asset positions as-built (asset survey assets_20260726120533.xlsx, UTM 40N / EPSG:32640).
2. AGL works demarcation (red) drawn around field-verified affected assets (+2.0 m) — field condition governs.
3. Secondary cables: no joints — full manhole-to-light replacement. Confirm routes vs AGL duct-layout CAD (Rev C) before works.
4. Isolate, lock out & prove dead all listed circuits at CCR under permit before any cutting, coring or excavation.
5. Reinstatement setting-out by civil survey from as-built E/N, checked against adjacent undisturbed fittings before coring.
LEGEND — WORKS ACTIONS (THIS SHEET)
NEW SEC. CABLE ONLY (DUCT) — outer blue / inner green
RRM — REMOVE / PROTECT / RE-FIX (magenta / white)
EXISTING AGL ASSET (AS-BUILT)
SECONDARY DUCT RUN CROSSING CUT (INDICATIVE)
AGL WORKS DEMARCATION (GOVERNING)
TAXIWAY CENTERLINE (AS-BUILT, THROUGH TCC FITTINGS)
STOP BAR (AS-BUILT, THROUGH SBC FITTINGS)
TWY EDGE / PAVEMENT BOUNDARY (INDICATIVE 23 m — CONFIRM ON SITE)

## Slide 4
SHOP DRAWING — ELECTRICAL / AGL SCOPE (FIELD-GOVERNED) · TAXIWAY E (E4–E6) — LOCATION 3 · DWG NO AUH-SK-AGL-TWYE-001-1003 REV P06
UTM 40N (EPSG:32640) — AS-BUILT POSITIONS · DO NOT SCALE FROM DRAWING
AGL WORKS DEMARCATION — PER FIELD-VERIFIED AFFECTED ASSETS (614.4 m²)
RRM.283
P4.036.399
TCCECH.04.005
TCCECH.04.004
RRM.547
RRM.548
RRM.558
RRM.559
RRM.655
RRM.669
HH.E.144
TCCECH.03.006
TCCECH.03.004
TCCECH.03.005
TCCECH.05.034
TCCECH.05.033
TCCECH.06.035
TCCECH.06.036
EL.EBASE.13328
EL.EBASE.13329
EL.EBASE.13330
EL.EBASE.13331
TCC102.01.052
TCC102.02.050
TCCECH.03.001
TCCECH.05.016
TCCECH.05.017
TCCECH.06.019
TCCECH.06.017
TCCECH.06.018
TCCECH.04.001
TCCECH.05.018
P4.037
P4.039
HH.E.057
HH.E.061
HH.E.060
HH.E4.010
HH.E.058
HH.E.059
P4.041
MH.E.015
MH.E.023
SGC102.02.015
SGC102.02.014
SBC102-01/038
SBC102-01/039
SBC102-02/035
SBC102-02/036
SBC102-01/040
SBC102-01/041
SBC102-02/037
SBC102-02/038
TCCECH-03/002
TCCECH-04/002
TCCECH-03/003
TCCECH-04/003
RRM.557
RRM.670
LOCATION 3 — 1003 · REV P06 (ISSUED)
SCOPE PER FIELD SHEET Second_milling_area rev _1 — FIELD CONDITION GOVERNS (supersedes the earlier no-works revision)
Sheet A3 (420 x 297 mm) · NOT TO SCALE — approx. 1:465 as plotted · UTM 40N · Issued 28.07.2026 · Prepared: Mohammed, AGL Team Leader — ADB SAFEGATE · Approved: Ragesh Menon, AGL Manager
SCOPE / QUANTITIES (PER FIELD VERIFICATION)
SHALLOW BASE AFFECTED — NO CORING; DUMMY PLATE + CABLE (SAWCUT): 4 No.
• SBC102-01/038, 01/039, 02/035, 02/036 (EP7 STOP BAR)
NEW SECONDARY CABLE ONLY (VIA DUCT): 8 No.
• SBC102-01/040, 01/041, 02/037, 02/038, TCCECH-03/002, 04/002, 03/003, 04/003
RRM.557 (0.07 m — treat as within works) & RRM.670: REMOVE / PROTECT / RE-FIX
ISOLATE CIRCUITS: SBC102.01/.02, TCCECH.03/.04
DUMMY PLATES: 4 No. — NO CORING HERE; BASES RETAINED & BLANKED (BLACK SQUARE)
GENERAL NOTES
1. All asset positions as-built (asset survey assets_20260726120533.xlsx, UTM 40N / EPSG:32640).
2. AGL works demarcation (red) drawn around field-verified affected assets (+2.0 m) — field condition governs.
3. Secondary cables: no joints — full manhole-to-light replacement. Confirm routes vs AGL duct-layout CAD (Rev C) before works.
4. Isolate, lock out & prove dead all listed circuits at CCR under permit before any cutting, coring or excavation.
5. Reinstatement setting-out by civil survey from as-built E/N, checked against adjacent undisturbed fittings before coring.
LEGEND — WORKS ACTIONS (THIS SHEET)
BASE RETAINED + DUMMY PLATE + NEW CABLE (SAWCUT) — outer amber / inner orange
NEW SEC. CABLE ONLY (DUCT) — outer blue / inner green
RRM — REMOVE / PROTECT / RE-FIX (magenta / white)
EXISTING AGL ASSET (AS-BUILT)
SECONDARY DUCT RUN CROSSING CUT (INDICATIVE)
AGL WORKS DEMARCATION (GOVERNING)
TAXIWAY CENTERLINE (AS-BUILT, THROUGH TCC FITTINGS)
STOP BAR (AS-BUILT, THROUGH SBC FITTINGS)
TWY EDGE / PAVEMENT BOUNDARY (INDICATIVE 23 m — CONFIRM ON SITE)
FITTING LIFTED, OPENING PROTECTED DURING MILLING — black square

## Slide 5
CONSOLIDATED FIELD-GOVERNED SCOPE — TWY E (E4–E6)
Loc | Asset | Works Action | Route | Remarks
LOC-01 | SBC102-02/024 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/027 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/025 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/028 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/026 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | SBC102-01/029 | CORE OUT + NEW CABLE | Duct | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/034 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-03/036 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/035 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-03/037 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | TCCECH-04/036 | CORE OUT + NEW CABLE | Sawcut | Core out shallow base + full cable replacement
LOC-01 | SBC102-02/027 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-01 | TCCECH-03/035 | DUMMY PLATE + NEW CABLE | Sawcut | Field: base NOT affected — fitting lifted, dummy plate fitted, full cable replacement
LOC-01 | TCCECH-03/018 | DUMMY PLATE + NEW CABLE | Sawcut | Field: base NOT affected — fitting lifted, dummy plate fitted, full cable replacement
LOC-01 | TCC103-11/021 | DUMMY PLATE + NEW CABLE | Sawcut | Cable crosses cut (2.0 m in cut) — fitting lifted, dummy plate, full cable replacement
LOC-01 | TCC103-11/126 | DUMMY PLATE + NEW CABLE | Sawcut | Cable crosses cut (2.0 m in cut) — fitting lifted, dummy plate, full cable replacement
LOC-01 | TCC103-12/021 | DUMMY PLATE + NEW CABLE | Sawcut | Cable crosses cut (2.0 m in cut) — fitting lifted, dummy plate, full cable replacement
LOC-01 | TCC103-12/022 | DUMMY PLATE + NEW CABLE | Sawcut | Cable crosses cut (7.8 m in cut) — fitting lifted, dummy plate, full cable replacement
LOC-01 | SBC102-01/026 | NOT AFFECTED |  | 
LOC-02 | TCCECH-03/007 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-04/007 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-03/008 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-04/008 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | TCCECH-03/009 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-02 | RRM.555 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving
LOC-03 | SBC102-01/038 | DUMMY PLATE + NEW CABLE | Sawcut | Base retained — fitting lifted, dummy plate fitted, full cable replacement
LOC-03 | SBC102-01/039 | DUMMY PLATE + NEW CABLE | Sawcut | Base retained — fitting lifted, dummy plate fitted, full cable replacement
LOC-03 | SBC102-02/035 | DUMMY PLATE + NEW CABLE | Sawcut | Base retained — fitting lifted, dummy plate fitted, full cable replacement
LOC-03 | SBC102-02/036 | DUMMY PLATE + NEW CABLE | Sawcut | Base retained — fitting lifted, dummy plate fitted, full cable replacement
LOC-03 | SBC102-01/040 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-01/041 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/037 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | SBC102-02/038 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-03/002 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-04/002 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-03/003 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | TCCECH-04/003 | NEW CABLE ONLY | Duct | Full manhole-to-light cable replacement
LOC-03 | RRM.557 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving
LOC-03 | RRM.670 | RRM REMOVE / PROTECT | — | Remove / protect before sawcut, re-fix after paving

## Slide 6
CONSOLIDATED SCOPE TOTALS — TWY E (E4–E6)
1,887.3 m²
Total demarcation area
11
Core-outs (LOC-01 only)
10
Dummy plates (6 confirmed + 4 provisional)
35
Secondary cable runs
3
RRMs
1
Field-verified not affected
PROVISIONAL — TCC103 (4 No.)
DEMARCATION AREA BY LOCATION
LOC-01 (sheet 1001) — 572.6 m² LOC-02 (sheet 1002) — 700.3 m² LOC-03 (sheet 1003) — 614.4 m² Total — 1,887.3 m²
15
Saw-cut route runs
LOC-01: 11 • LOC-03: 4 • 13.8 m of secondary cable inside the cut
20
Duct route runs (secondary cable)
LOC-01: 7 • LOC-02: 5 • LOC-03: 8 • existing duct, pulled manhole-to-light
TCC103-11/021 — dummy plate, cable crosses cut (2.0 m)
TCC103-11/126 — dummy plate, cable crosses cut (2.0 m)
TCC103-12/021 — dummy plate, cable crosses cut (2.0 m)
TCC103-12/022 — dummy plate, cable crosses cut (7.8 m)